## Coversheet
[6 empty] | Document No.: | ESS-
|  | HAZOP RECORD SHEET |  |  |  | Project No.: | WP16
ESS WP16
List of HAZOP Participants
Name |  |  |  | Position |  |  | Attendance Date
Attachments
Revisions
X | 2
1
Status | Revision | Date | Description |  | Issued | Approved | Released

## HEBT-A2T
Components | LWUs (quadrapole magnets, beam instrumentation) Quadrapole and Dipole magnets
Number | Key word | Deviation | Possible causes | Consequence | Existing safeguards | Comments & recommendations
1 | flow | high | - Malfunction of the pump - Malfunction of one of the flow meters (e.g. FIT010, FIT000) - failure of the PLC | - Cooling performance of the system increased - potential trip/alarm of the skid - Induced mechanical vibrations - low efficiency in terms of energy consumption | - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. PLC error) - flow meters on the cooling skid (e.g. FIT010, FIT000)
2 |  | low | - Malfunction of the pump - Malfunction of one of the flow meters (e.g. FIT010, FIT000) - failure of the PLC - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - flow meters on the cooling skid (e.g. FIT010, FIT000) - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify if signal from flow switches should lead to trip or alarm
3 |  | zero | - Pump failure - failure of the PLC - malfunction of one of the flow switches - Electrical power cut - leak(s) in cooling circuit | - Overheating of the LINAC systems (e.g.quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify the needs for UPS for the controls with ICS - clarify if signal from flow switches should lead to trip or alarm
4 |  | unstable | - Malfunction of the pump - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - redundancy of the pumps (PIA & PIB) - alarm on skid (e.g. pump error, low flow) - trip of the cooling skid (e.g. low flow) | - clarify if signal from flow switches should lead to trip or alarm
5 |  | reverse | - Unexpected closing of the pneumatic valves (e.g. V009, V012) due to loss of instrument air - Unexpected closing of gate valves (e.g. V011, V010, V019) | - Overheating of the LINAC systems (e.g. quadrupole magnets) - erroneous flow switch signal - potential damage of the pumps - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. instrument error) - trip of the cooling skid (e.g. low flow) | - clarify fail-safe state of the valves --> fail open for V009, V012 & V022 - operators training - loss of instrument air should be monitored (pressure gauge) and part of the alarm systems '- clarify if signal from flow switches should lead to trip or alarm
6 | pressure | high | - closure of both isolation valves (eg. after maintenance) - malfunction of the pump - failure of the PLC - Unexpected closing of the pneumatic valves (e.g. V009, V012) due to loss of instrument air - Unexpected closing of gate valves (e.g. V011, V010, V019) | - potential damage of the LINAC systems (e.g magnet coils) - potential damage of the pumps - potential trip/alarm of the skid | - Pressure sensors on skid (PIT005 & PIT004) - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error, low flow) - trip of the cooling skid (e.g. low flow, PLC error) | - Unlikely to have excessive pressure at single components - clarify fail-safe state of the valves --> fail open for V009, V012 & V022 - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
7 |  | low | - Malfunction of the pump - leak(s) in cooling circuit - malfunction of one of the pressure sensor (e.g. PIT004, PIT005) - failure of the PLC | - cooling performance of the system decreased - overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - Pressure sensors on skid (PIT005 & PIT004) - alarm on skid (e.g. pump error, PLC error, instrument error, low flow) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
8 |  | zero | - Pump failure - failure of the PLC - Electrical power cut - leak(s) in cooling circuit | - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - pressure sensors on skid (PIT005 & PIT004) | - clarify if signal from flow switches should lead to trip or alarm - clarify the needs for UPS for the controls with ICS - additional pressure sensors to be installed downstream LINAC systems
9 |  | unstable | - Malfunction of the pump - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - redundancy of the pumps (PIA & PIB) - alarm on skid (e.g. pump error, low flow) - trip of the cooling skid (e.g. low flow) - pressure sensors on skid (PIT005 & PIT004)) | - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
10 | temperature | high | - skid failure (heat exchanger) - malfunction of one of the temperature sensors (TT001, TT03) - wrong set point defined by the operator | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - trip of the cooling skid (e.g. high temperature) - alarm on skid (e.g. high temperature, instrument error) - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems | operators training
11 |  | low | - skid failure (heat exchanger) - malfunction of one of the temperature sensors (TIT001, TIT002, TIT03) - wrong set point defined by the operator | - CWS01 -> potentially 8 °C water to IS/LEBT/MEBT/DTL FC - CWS02 -> potentially 25 °C to couplers & quads -> no impact - potential impact on the performances of the LINAC - potential alarm of the skid | - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems - alarm on skid (e.g. instrument error) | operators training
12 |  | unstable | - skid failure (heat exchanger) - wrong set point defined by the operator | - Cooling performance of the system decreased. - potential overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems - trip of the cooling skid (e.g. high temperature) - alarm on skid (e.g. high temperature, instrument error) | operators training
13 | water quality | low (high conductivity, particles) | - failure of skid deminineralizer - corrosion in pipes - filters clogged (F001 & F002) | - lower lifetime, potential clogging -> low flow - Performance of the LINAC systems affected? - potential trip/alarm of the skid | - periodical maintenance of the filters and pipes - alarm on skid (e.g. filter replacement, high conductivity) - trip of the cooling skid (e.g. high conductivity)
14 | corrosion | excessive | - poor maintenance - poor corrosion protection - inadequate selection of materials - failure of the degassing unit | - cooling performance of the system decreased. - leak(s) in cooling circuit | - stainless steel pipes? - degassing unit - regular maintenace and inspection
15 | mechanical vibration | excessive | - pump control failure (frequency?) - pump failure | break of LINAC system (e.g.magnets) | to be filled by Anton & Akif (limit on the frequency of the pumps, etc.)
16 | loss of confinement |  | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves | - water leaks - potential exposure of personnel to activated water | to be filled by Anton & Akif (leak tightness verificiation, pressure test, non-destructive tests of welding, etc.) | operators training
17 | release fo activated water | uncontrolled | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves - excessive degassing |  |  | regular monitoring of the tritium level of the water by waste water Group
18 | contact with hot surfaces |  | maintenance of equipment | possible injuries (burns) |  | - operators training - instruction manual - labeling of hot surfaces - consider protective insulation of hot surfaces

## Cold Linac
Components | RF couplers (Spoke, elliptical) LWU quadrapole magnets (Q5, Q6)
Number | Key word | Deviation | Possible causes | Consequence | Existing safeguards | Comments & recommendations
1 | flow | high | - Malfunction of the pump - Malfunction of one of the flow meters (e.g. FIT010, FIT000) - failure of the PLC | - Cooling performance of the system increased - potential trip/alarm of the skid - Induced mechanical vibrations - low efficiency in terms of energy consumption | - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. PLC error) - flow meters on the cooling skid (e.g. FIT010, FIT000)
2 |  | low | - Malfunction of the pump - Malfunction of one of the flow meters (e.g. FIT010, FIT000) - failure of the PLC - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - flow meters on the cooling skid (e.g. FIT010, FIT000) - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify if signal from flow switches should lead to trip or alarm
3 |  | zero | - Pump failure - failure of the PLC - malfunction of one of the flow switches - Electrical power cut - leak(s) in cooling circuit | - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify the needs for UPS for the controls with ICS - clarify if signal from flow switches should lead to trip or alarm
4 |  | unstable | - Malfunction of the pump - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - redundancy of the pumps (PIA & PIB) - alarm on skid (e.g. pump error, low flow) - trip of the cooling skid (e.g. low flow) | - clarify if signal from flow switches should lead to trip or alarm
5 |  | reverse | - Unexpected closing of the pneumatic valves (e.g. V009, V012) due to loss of instrument air - Unexpected closing of gate valves (e.g. V011, V010, V019) | - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - erroneous flow switch signal - potential damage of the pumps - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. instrument error) - trip of the cooling skid (e.g. low flow) | - clarify fail-safe state of the valves --> fail open for V009, V012 & V022 - operators training - loss of instrument air should be monitored (pressure gauge) and part of the alarm systems '- clarify if signal from flow switches should lead to trip or alarm
6 | pressure | high | - closure of both isolation valves (eg. after maintenance) - malfunction of the pump - failure of the PLC - Unexpected closing of the pneumatic valves (e.g. V009, V012) due to loss of instrument air - Unexpected closing of gate valves (e.g. V011, V010, V019) | - potential damage of the LINAC systems (e.g magnet coils) - potential damage of the pumps - potential trip/alarm of the skid | - Pressure sensors on skid (PIT005 & PIT004) - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error, low flow) - trip of the cooling skid (e.g. low flow, PLC error) | - Unlikely to have excessive pressure at single components - clarify fail-safe state of the valves --> fail open for V009, V012 & V022 - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
7 |  | low | - Malfunction of the pump - leak(s) in cooling circuit - malfunction of one of the pressure sensor (e.g. PIT004, PIT005) - failure of the PLC | - cooling performance of the system decreased - overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - Pressure sensors on skid (PIT005 & PIT004) - alarm on skid (e.g. pump error, PLC error, instrument error, low flow) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
8 |  | zero | - Pump failure - failure of the PLC - Electrical power cut - leak(s) in cooling circuit | - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - pressure sensors on skid (PIT005 & PIT004) | - clarify if signal from flow switches should lead to trip or alarm - clarify the needs for UPS for the controls with ICS - additional pressure sensors to be installed downstream LINAC systems
9 |  | unstable | - Malfunction of the pump - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - redundancy of the pumps (PIA & PIB) - alarm on skid (e.g. pump error, low flow) - trip of the cooling skid (e.g. low flow) - pressure sensors on skid (PIT005 & PIT004)) | - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
10 | temperature | high | - skid failure (heat exchanger) - malfunction of one of the temperature sensors (TT001, TT03) - wrong set point defined by the operator | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - trip of the cooling skid (e.g. high temperature) - alarm on skid (e.g. high temperature, instrument error) - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems | operators training
11 |  | low | - skid failure (heat exchanger) - malfunction of one of the temperature sensors (TIT001, TIT002, TIT03) - wrong set point defined by the operator | - CWS01 -> potentially 8 °C water to IS/LEBT/MEBT/DTL FC - CWS02 -> potentially 25 °C to couplers & quads -> no impact - potential impact on the performances of the LINAC - potential alarm of the skid | - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems - alarm on skid (e.g. instrument error) | operators training
12 |  | unstable | - skid failure (heat exchanger) - wrong set point defined by the operator | - Cooling performance of the system decreased. - potential overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems - trip of the cooling skid (e.g. high temperature) - alarm on skid (e.g. high temperature, instrument error) | operators training
13 | water quality | low (high conductivity, particles) | - failure of skid deminineralizer - corrosion in pipes - filters clogged (F001 & F002) | - lower lifetime, potential clogging -> low flow - Performance of the LINAC systems affected? - potential trip/alarm of the skid | - periodical maintenance of the filters and pipes - alarm on skid (e.g. filter replacement, high conductivity) - trip of the cooling skid (e.g. high conductivity)
14 | corrosion | excessive | - poor maintenance - poor corrosion protection - inadequate selection of materials - failure of the degassing unit | - cooling performance of the system decreased. - leak(s) in cooling circuit | - stainless steel pipes? - degassing unit - regular maintenace and inspection
15 | mechanical vibration | excessive | - pump control failure (frequency?) - pump failure | break of LINAC system (e.g.RF coupler, magnets) | to be filled by Anton & Akif (limit on the frequency of the pumps, etc.)
16 | loss of confinement |  | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves | - water leaks - potential exposure of personnel to activated water | to be filled by Anton & Akif (leak tightness verificiation, pressure test, non-destructive tests of welding, etc.) | operators training
17 | release fo activated water | uncontrolled | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves - excessive degassing |  |  | regular monitoring of the tritium level of the water by RadioProtection Group
18 | contact with hot surfaces |  | maintenance of equipment | possible injuries (burns) |  | - operators training - instruction manual - labeling of hot surfaces - consider protective insulation of hot surfaces

## Warm Linac
Components | IS (High voltage platform) LEBT (magnets, beam instrumentation) MEBT (magnets, beam instrumentation, Buncher cavitites) DTL FC (faraday cups - beam instrumentation)
Number | Key word | Deviation | Possible causes | Consequence | Existing safeguards | Comments & recommendations
1 | flow | high | - Malfunction of the pump - Malfunction of one of the flow meters (e.g. FIT010, FIT000) - failure of the PLC | - Cooling performance of the system increased - potential trip/alarm of the skid - Induced mechanical vibrations - low efficiency in terms of energy consumption | - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. PLC error) - flow meters on the cooling skid (e.g. FIT010, FIT000)
2 |  | low | - Malfunction of the pump - Malfunction of one of the flow meters (e.g. FIT010, FIT000) - failure of the PLC - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - flow meters on the cooling skid (e.g. FIT010, FIT000) - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify if signal from flow switches should lead to trip or alarm
3 |  | zero | - Pump failure - failure of the PLC - malfunction of one of the flow switches - Electrical power cut - leak(s) in cooling circuit | - Overheating of the LINAC systems (e.g.quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify the needs for UPS for the controls with ICS - clarify if signal from flow switches should lead to trip or alarm
4 |  | unstable | - Malfunction of the pump - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - redundancy of the pumps (PIA & PIB) - alarm on skid (e.g. pump error, low flow) - trip of the cooling skid (e.g. low flow) | - clarify if signal from flow switches should lead to trip or alarm
5 |  | reverse | - Unexpected closing of the pneumatic valves (e.g. V009, V012) due to loss of instrument air - Unexpected closing of gate valves (e.g. V011, V010, V019) | - Overheating of the LINAC systems (e.g. quadrupole magnets) - erroneous flow switch signal - potential damage of the pumps - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. instrument error) - trip of the cooling skid (e.g. low flow) | - clarify fail-safe state of the valves --> fail open for V009, V012 & V022 - operators training - loss of instrument air should be monitored (pressure gauge) and part of the alarm systems '- clarify if signal from flow switches should lead to trip or alarm
6 | pressure | high | - closure of both isolation valves (eg. after maintenance) - malfunction of the pump - failure of the PLC - Unexpected closing of the pneumatic valves (e.g. V009, V012) due to loss of instrument air - Unexpected closing of gate valves (e.g. V011, V010, V019) | - potential damage of the LINAC systems (e.g magnet coils) - potential damage of the pumps - potential trip/alarm of the skid | - Pressure sensors on skid (PIT005 & PIT004) - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error, low flow) - trip of the cooling skid (e.g. low flow, PLC error) | - Unlikely to have excessive pressure at single components - clarify fail-safe state of the valves --> fail open for V009, V012 & V022 - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
7 |  | low | - Malfunction of the pump - leak(s) in cooling circuit - malfunction of one of the pressure sensor (e.g. PIT004, PIT005) - failure of the PLC | - cooling performance of the system decreased - overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - Pressure sensors on skid (PIT005 & PIT004) - alarm on skid (e.g. pump error, PLC error, instrument error, low flow) - trip of the cooling skid (e.g. low flow, PLC error) | - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
8 |  | zero | - Pump failure - failure of the PLC - Electrical power cut - leak(s) in cooling circuit | - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - alarm on skid (e.g. pump error, PLC error, instrument error) - redundancy of the pumps (PIA & PIB) - pressure sensors on skid (PIT005 & PIT004) | - clarify if signal from flow switches should lead to trip or alarm - clarify the needs for UPS for the controls with ICS - additional pressure sensors to be installed downstream LINAC systems
9 |  | unstable | - Malfunction of the pump - leak(s) in cooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - flow switches located downstream each LINAC system - redundancy of the pumps (PIA & PIB) - alarm on skid (e.g. pump error, low flow) - trip of the cooling skid (e.g. low flow) - pressure sensors on skid (PIT005 & PIT004)) | - clarify if signal from flow switches should lead to trip or alarm - additional pressure sensors to be installed downstream LINAC systems
10 | temperature | high | - skid failure (heat exchanger) - malfunction of one of the temperature sensors (TT001, TT03) - wrong set point defined by the operator | - Cooling performance of the system decreased. - Overheating of the LINAC systems (e.g. quadrupole magnets) - potential trip/alarm of the skid | - trip of the cooling skid (e.g. high temperature) - alarm on skid (e.g. high temperature, instrument error) - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems | operators training
11 |  | low | - skid failure (heat exchanger) - malfunction of one of the temperature sensors (TIT001, TIT002, TIT03) - wrong set point defined by the operator | - CWS01 -> potentially 8 °C water to IS/LEBT/MEBT/DTL FC - CWS02 -> potentially 25 °C to couplers & quads -> no impact - potential impact on the performances of the LINAC - potential alarm of the skid | - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems - alarm on skid (e.g. instrument error) | operators training
12 |  | unstable | - skid failure (heat exchanger) - wrong set point defined by the operator | - Cooling performance of the system decreased. - potential overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - potential trip/alarm of the skid | - temperature sensors on cooling skid (e.g. TIT001, TIT002, TIT003) and downstream some LINAC systems - trip of the cooling skid (e.g. high temperature) - alarm on skid (e.g. high temperature, instrument error) | operators training
13 | water quality | low (high conductivity, particles) | - failure of skid deminineralizer - corrosion in pipes - filters clogged (F001 & F002) | - lower lifetime, potential clogging -> low flow - Performance of the LINAC systems affected? - potential trip/alarm of the skid | - periodical maintenance of the filters and pipes - alarm on skid (e.g. filter replacement, high conductivity) - trip of the cooling skid (e.g. high conductivity)
14 | corrosion | excessive | - poor maintenance - poor corrosion protection - inadequate selection of materials - failure of the degassing unit | - cooling performance of the system decreased. - leak(s) in cooling circuit | - stainless steel pipes? - degassing unit - regular maintenace and inspection
15 | mechanical vibration | excessive | - pump control failure (frequency?) - pump failure | break of LINAC system (e.g.magnets) | to be filled by Anton & Akif (limit on the frequency of the pumps, etc.)
16 | loss of confinement |  | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves | - water leaks - potential exposure of personnel to activated water | to be filled by Anton & Akif (leak tightness verificiation, pressure test, non-destructive tests of welding, etc.) | operators training
17 | release fo activated water | uncontrolled | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves - excessive degassing |  |  | regular monitoring of the tritium level of the water by waste water Group
18 | contact with hot surfaces |  | maintenance of equipment | possible injuries (burns) |  | - operators training - instruction manual - labeling of hot surfaces - consider protective insulation of hot surfaces