## Slide 1: Vacuum Control System
Hilko Spoelstra
Vacuum Systems Engineer
Vacuum System Section – STS/AD
www.europeanspallationsource.se
23 March, 2017

## Slide 2: Outline
Overview
Requirements
Interfaces
Vacuum Control System in more detail
Status as today
Conclusion
Note: The presentation will focus mainly on the vacuum control system for the LINAC. Target and Instruments are still not on the same detailed phase as the Accelerator although the concept is assumed to be the same for all systems.

## Slide 3: LINAC Vacuum System
Source
LEBT
RFQ
MEBT
DTL
Spokes
Med. β
High β
HEBT

## Slide 4: Vacuum Equipment Summary for the accelerator
Standardization of vacuum equipment through the Framework Agreement (FA), which is in process now
FA contract to be signed by the middle of May 2017
Single suppliers for each type of equipment
Framework agreement even applicable for our in-kind STFC Daresburry and CEA Saclay.

## Slide 5: Vacuum Control System
Complete in-house design for racks and controls
  Vacuum Group - > Hardware and Electronic design (EPLAN)
  Integrated Control System -> PLC and EPICS IOC programming
Common approach for all vacuum systems, Accelerator, Target and Neutron Instruments

## Slide 6: Requirements
The vacuum control system shall be able to:
  Control the complete vacuum system remotely through different access points
  Act in a safe way on abnormalities in the vacuum system (internal or external sources)
  Display and archive the status and readouts from all the vacuum instrumentation. Ex: gauges, pumps and valves
  Archive the vacuum pressure for the entire LINAC during the event of a power failure
  Provide an interface to the Machine Protection System (MPS)

## Slide 7: Design criteria
  Vacuum is a relative slow system:
    Response time for interlocks on gauges > 10 ms.
    Response time for normal gate valves > 1 s (fast valves ≈ 15 ms.)
  No electronics allowed in the accelerator tunnel - All control electronics must be separated from their devices (pumps, gauges, etc.)
  Controllers will be installed in control racks in radiation safe locations in the Gallery and FEB rack area (distance up to 100 m)

## Slide 8: Interfaces
Integrated Control System
  Vacuum Skeleton - ESS-0004789 - System Requirements Specification
  Vacuum Skeleton - ESS-0004790 - Concept Of Operation
  Vacuum Skeleton - ESS-0004793 - Interface description
  Vacuum Skeleton - ESS-0061017 - System Verification Plan
Machine Protection System
  Machine Protection and Vacuum System Interface Control Document (to be released in CHESS soon)
Electrical support
  Rack Requirements/Power requirements
  Rack Location
  Cable database
RF system
  One interlock signal for each gauge on all RF couplers (exact interface tbd.)

## Slide 9: Interface: Vacuum Operation PLC & EPICS
PLC:
-Drive controller -Local protection
-Data Acquisition -Beam Permit
EPICS:
-Control panels, trending
-Real-time Data Acquisition
-Data Logging
-Serial communication with the Controllers
Vacuum Control Architecture
Network Communication

## Slide 10: Sector Gate Valves and MPS
Automatic closure of the sector gate valves is triggered by configurable output relays from specific gauge and pump controllers
Signals will be mixed according a voting plan programmed within the PLC
Vacuum Interlock PLC
MPS system looks at Vacuum Beam Permits and sector gate valves
MPS PLC System
24 Vdc
Beam Permit 1
Beam Permit 2
Redundancy

## Slide 11: Status as today
Prototype vacuum control rack
  Designed and assembled at ESS
  Successfully installed by ESS at in-kind partner institute IFNF Catania for testing on the LEBT
  Controls through EPICS
  It is the base concept for all vacuum control racks
Second prototype is planed for Q2
  Framework Agreement for the racks and Vacuum Equipment to be in place
  Taking in account the ESS Electrical Standardization Catalogue

## Slide 12: Status as today (cont.)
Facility Breakdown Structure and ESS naming in place for all LINAC vacuum parts
Working on the detailed design of the 54 control racks in EPLAN
Cable database ready
Rack assembly space in RATS will be started Q2 2017
  Assembly of the racks
  Preliminary rack tests

## Slide 13: Conclusion
  The ESS vacuum control system is designed in-house by the Vacuum Group and the Integrated Control System Group
  All interfaces were listed and clear definitions of the requirements done
  The vacuum control system is based on PLC and EPICS IOC
    EPICS for the control screens, configuration and post-analysis
    PLCs handle safety functionality in the vacuum system
  The first prototype vacuum control rack was designed and assembled by the ESS Vacuum group and ICS and installed successfully at our in-kind partner institute, INFN in Catania
  Next step: set up and start up of the vacuum rack assembly area at RATS