## Slide 1: ICS Update @ 3rd ESS Beam Diagnostics Forum
Simone Farina & Jeong Han Lee
Integrated Control System Division
www.europeanspallationsource.se
2017-04-26

## Slide 2: Outline
MicroTCA overview;
MTCA Carrier Hub;
MicroTCA infrastructure:
MTCA crates;
Power Modules;
Advanced Mezzanine Cards:
MRF Event Receiver;
CPU cards;
IOxOS IFC1410/IFC1420;
Software Stacks / Showcase

## Slide 3: MicroTCA Overview
Glossary:
PM : Power Module
MicroTCA : Micro Telecommunication Computing Architecture
MCH : MicroTCA Carrier Hub
  manages the other boards, provides interconnection switch capabilities, clock distribution, etc
CU : Cooling Unit
AMC : Advanced Mezzanine Card
  basic constituent of the MTCA system, can provide support for a RTM
RTM : Rear Transition Module
  provides real estate area for additional electronics
MMC : Module Management Controller
  monitors the status of the AMC
MCMC : MicroTCA Carrier Management Controller;

## Slide 4: MicroTCA Overview
Why MicroTCA ?
“MicroTCA is a modular standard.
By configuring highly diverse collections of AdvancedMCs in a MicroTCA Shelf, many different application architectures can be easily realized.
The common elements defined by MicroTCA are capable of interconnecting these AdvancedMCs in many interesting ways—powering and managing them, all at high efficiency and low cost.”

## Slide 5: MicroTCA Infrastructure

## Slide 6: MicroTCA Chassis (1)
Need to support 2 different chassis types:
12 slots 9U for systems requiring more than 6 AMCs and/or more than 4 RTMs;
Tradeoffs:
Front to rear cooling scheme
6 slots 3U to reduce the number of racks deployed.
Supported Components | 9U | 3U
MCH(s) | 2 | 1
PM(s) | 4 (3+1) | 2
CU(s) | 2 (push-pull) | 2 (pull only)
AMC(s) | 12 | 6
RTM(s) | 12 | 4

## Slide 7: MicroTCA Chassis (2)
9U backplane interconnections:
2 GbE links (1 towards each MCH)
4x LVDS type AMC to AMC links (BP specific)
Redundant PCIe 4x
2 high speed AMC to AMC links (BP specific)
8x MLVDS lanes
4x AMC Clock input lines (2 for each MCH)
1x FAT Pipe Reference CLK

## Slide 8: MicroTCA Chassis (3)
3U backplane interconnections:
2 GbE links
4x LVDS type AMC to AMC links
PCIe 8x and 4x
2 high speed AMC to AMC links (BP specific)
8x MLVDS lanes
2x AMC Clock lines
1x FAT Pipe Reference CLK
New backplane design (available week 26):
PCIe 8x to all AMCs
4x LVDS AMC to AMC provided to all slots
8x MLVDS lanes span all AMCs

## Slide 9: MicroTCA Chassis (3)
3U backplane interconnections:
2 GbE links
4x LVDS type AMC to AMC links
PCIe 8x and 4x
2 high speed AMC to AMC links (BP specific)
8x MLVDS lanes
2x AMC Clock lines
1x FAT Pipe Reference CLK

## Slide 10: MicroTCA Chassis (3)
3U backplane interconnections:
2 GbE links
4x LVDS type AMC to AMC links
PCIe 8x and 4x
2 high speed AMC to AMC links (BP specific)
8x MLVDS lanes
2x AMC Clock lines
1x FAT Pipe Reference CLK
New backplane design (available week 26):
PCIe 8x to all AMCs
4x LVDS AMC to AMC provided to all slots
8x MLVDS lanes span all AMCs
Old COTS design

## Slide 11: MicroTCA MCH & PM
MicroTCA Carrier Hub :
N.A.T. , MCMC implementation offers broad compatibility
Power Modules:
Wiener (1KW)
N.A.T. (600W)
Both will be used. Choice according to:
Redundancy;
Noise requirements;
PCIe gen.3 48 port switch;
GbE switch;
Clock input/output on backplane CLK1 and CLK2 plus front panel SMA;
IPMI message forwarding on GbE;

## Slide 12: MicroTCA AMC boards: EVR
Timing system based on Micro-Research Finland products:
clocks from/to TCLKA/TCLKB
24 differential lanes to RTM (no RTM designed yet)
driving/receiving differential triggers AMC RX/TX ports 17 to 20 (MLVDS)
front panel 4 x TTL outputs, 2 x TTL inputs (to be replaced by UIO modules)
VHDCI front panel connector for IFB-300 interface box
Delay compensation and feedback

## Slide 13: MicroTCA AMC boards: CPU
Concurrent Technologies AM900:
Intel i7 x86-64 architecture
PCIe upstream
Up to 16GB DDR3 memory
T208x Freescale PPC architecture
2GB DDR3 memory
PCIe EP (upstream capability under development)
IOxOS IFC1410/1411:
FMC support (2 HPC IFC1410 / 1 HPC IFC1411)
ADC onboard (10ch IFC1420 only)
RTM support (D1.4 IFC1410 / A1.1 IFC1411)
Xilinx Kintex Ultrascale FPGA

## Slide 14: MicroTCA AMC boards: IFC14xx
IFC1410 block diagram :
MMC & sensors section;
PPC CPU section;
Configuration management;
Main FPGA/application
specific section;

## Slide 15: MicroTCA AMC boards: IFC14xx
IFC1410 Firmware infrastructure:
Every agent SW has two master and slave interfaces for request and response communications;
Communication based on PCIe TLPs
Separate Data and Control interconnect infrastructure;
Data:
Full mesh switch;
Master and slave interfaces for each agent switch;
Round Robin arbiter to assign bus mastership
IO Control:
Shared parallel bus;

## Slide 16: MicroTCA system example
Timing:
MCH:
AMC & RTM:
CPU:
Phase reference
Timing
Interlock
LAN
Ethernet
Control (PCIe)
Triggers
LO
Signals from:
PowerAmp
Cavity
PreAmp
VM
Clocks
Gets synchronization info from external device and provides:
clock to MCH
triggers to all AMCs
machine configuration settings
Manages a subset of AMCs
configures and collects data from AMCs
runs EPICS IOCs
Monitors AMCs status, distributes clocks and provides interconnections
Application specific. May provide interlocks and information to MPS

## Slide 17: MTCA Software Stacks / 2017.04

## Slide 18: MTCA Software Stacks / Plan

## Slide 19: MTCA Systems Monitoring / Plan
Slow > 1 Hz
Read Only (very limited Write)
Most PDUs support SNMP
MTCA MCH supports
  RCMP (IPMI)
  SNMP
EPICS modules
  ipmiComm (SLAC)
  devSNMP (FRIB)
  snmpLib (RAON)
Existent Open Source Tools
  ZABBIX
  ICINGA
MTCA Infrastructure Monitoring System

## Slide 20: MicroTCA system Showcase