## RFLPS machine state
| Preconditions | Supervisions
| The signals or pre-conditions required to allow the Machine State executes the desired command | Signals or supervisions conditions required to allow the Machine State keeps the reached status |  | How the interlock system acts
|  |  | OFF (0) | HV Enable (Inhibit Mod) - OFF
RF Enable (pin diode open) - OFF
|  |  | All premissions are OFF, initial status | Solenoid PSU - OFF
Filament PSU - OFF
|  |  | The system release the remote hard-control of the Solenoid PSU from the PLC. The Solenoid controller can be handled locally | MPS Status - OFF
LLRF output enable - OFF
| TS2-010RFC:RFS-VacPS-001:I | TS2-010RFC:RFS-VacPS-001:I | AUX (1) | The PLC takes the control of the Solenoid PSU, no local control is allowed
| TS2-010RFC:RFS-VacPS-002:I | TS2-010RFC:RFS-VacPS-002:I
| TS2-010RFC:RFS-Main-001:EmSw | TS2-010RFC:RFS-Main-001:EmSw | The PLC takes the hard-control of the Solenoid PSU, no local control is allowed
| TS2-010RFC:RFS-Oil-001:LS | TS2-010RFC:RFS-Oil-001:LS | Filament (2) | Filament PS ON Command
| TS2-010RFC:RFS-Oil-001:TSH | TS2-010RFC:RFS-Oil-001:TSH |  | I-Reg set-point output enabled
| TS2-010RFC:RFS-Oil-001:LO | TS2-010RFC:RFS-Oil-001:LO | Waits the warming up time before set the FIL status
| TS2-010RFC:RFS-Main-001:TT | TS2-010RFC:RFS-Main-001:TT
| TS2-010RFC:RFS-Oil-001:FIS | TS2-010RFC:RFS-Oil-001:FIS | Requires the Filament controller remote option is activated locally
| TS2-010RFC:RFS-Oil-001:TT | TS2-010RFC:RFS-Oil-001:TT
| TS2-010RFC:RFS-Oil-002:TT | TS2-010RFC:RFS-Oil-002:TT
TS2-010RFC:RFS-FIL-001:PSU.I_SET
|  | TS2-010RFC:RFS-FIL-001:PSU | TS2-010RFC:RFS-FIL-001:PSU.ON_CMD
| TS2-010RFC:RFS-Kly-001:ES | TS2-010RFC:RFS-Kly-001:ES | Standby (3) | Solenoid PSU ON command
| TS2-010RFC:RFS-Oil-001:AS | TS2-010RFC:RFS-Oil-001:AS |  | I-Reg set-point output enabled
| TS2-010RFC:RFS-Sol-001:FIS | TS2-010RFC:RFS-Sol-001:FIS | Transmitter ready for HV Enable
| TS2-010RFC:RFS-Sol-001:TT | TS2-010RFC:RFS-Sol-001:TT
| TS2-010RFC:RFS-Coll-001:FIT | TS2-010RFC:RFS-Coll-001:FIT
| TS2-010RFC:RFS-Coll-001:TT | TS2-010RFC:RFS-Coll-001:TT
| TS2-010RFC:RFS-Body-001:FIS | TS2-010RFC:RFS-Body-001:FIS
| TS2-010RFC:RFS-Body-001:TT | TS2-010RFC:RFS-Body-001:TT
| TS2-010RFC:RFS-Kly-001:ShldIntact | TS2-010RFC:RFS-Kly-001:ShldIntact
TS2-010RFC:RFS-SolPS-001:PSU
TS2-010RFC:RFS-SolPS-002:PSU
SIM | TS2-010RFC:RFS-Coll-001:SW-CALC | TS2-010RFC:RFS-Coll-001:SW-CALC | HV (4) | HV Modulator permission ON
TS2-010RFC:RFS-FIM-001:HVenaStat
|  | TS2-010RFC:RFS-PSS-001:Ready | The PLC through a hardwired connection detects any change of the FIM status and updated the Machine Status | TS2-010RFC:RFS-Mod-001:HvEna
FIM | TS2-010RFC:RFS-VacPS-001:I-SP | TS2-010RFC:RFS-VacPS-001:I-SP | TS2-010RFC:RFS-SIM-001:HvEnaStat
| TS2-010RFC:RFS-VacPS-002:I-SP | TS2-010RFC:RFS-VacPS-002:I-SP
| TS2-010RFC:RFS-SolPS-001:Cur | TS2-010RFC:RFS-SolPS-001:Cur
| TS2-010RFC:RFS-SolPS-002:Cur | TS2-010RFC:RFS-SolPS-002:Cur
| TS2-010RFC:RFS-Mod-001:Ready | TS2-010RFC:RFS-Mod-001:Ready
| TS2-010RFC:RFS-SIM-001:HvEnaCmd | TS2-010RFC:RFS-SIM-001:HvEnaCmd
TS2-010RFC:RFS-Mod-001:Cur
TS2-010RFC:RFS-Mod-001:Vol
TS2-010RFC:RFS-Mod-001:PulseWidth
TS2-010RFC:RFS-Mod-001:RepRate
SIM | TS2-010RFC:RFS-DA-001:Ready | TS2-010RFC:RFS-DA-001:Ready | RF (5) | Pin-diode enable
| TS2-010RFC:RFS-SS-001:Shutter | TS2-010RFC:RFS-SS-001:Shutter |  | Informs to MPS the current status
| TS2-010RFC:RFS-ADR-001:CHA | TS2-010RFC:RFS-ADR-001:CHA | The PLC through a hardwired connection detects any change of the FIM status and updated the Machine Status
| TS2-010RFC:RFS-ADR-001:CHB | TS2-010RFC:RFS-ADR-001:CHB |  | TS2-010RFC:RFS-LLRF-001:OutEna
| TS2-010RFC:RFS-Circ-001:TT | TS2-010RFC:RFS-Circ-001:TT |  | TS2-010RFC:RFS-PinD-001:RfEna
| TS2-010RFC:RFS-Circ-001:FIS | TS2-010RFC:RFS-Circ-001:FIS
| TS2-001RFC:RFS-TCU-001:ES | TS2-001RFC:RFS-TCU-001:ES
| TS2-010RFC:RFS-Load-001:TT | TS2-010RFC:RFS-Load-001:TT
| TS2-010RFC:RFS-RLoad-001:TT | TS2-010RFC:RFS-RLoad-001:TT | TS2-010RFC:RFS-SIM-001:RfEnaStat
| TS2-010RFC:RFS-RLoad-001:FIT | TS2-010RFC:RFS-RLoad-001:FIT
TS2-010RFC:RFS-FIM-001:RFenaStat
FIM | TS2-010RFC:RFS-SIM-001:RfEnaCmd | TS2-010RFC:RFS-SIM-001:RfEnaCmd
| TS2-010RFC:RFS-LLRF-001:MonAlarm | TS2-010RFC:RFS-LLRF-001:MonAlarm
| TS2-010RFC:RFS-CAV-001:ChainReady | TS2-010RFC:RFS-CAV-001:ChainReady
TS2-010RFC:RFS-PwrS-110:DaPwrFwd
TS2-010RFC:RFS-ADR-201001:ItckStat
TS2-010RFC:RFS-DirC-001:PwrFwr
TS2-010RFC:RFS-DirC-001:PwrReflect
TS2-010RFC:RFS-DirC-001:PulseWidth
TS2-010RFC:RFS-DirC-001:RepRate
TS2-010RFC:RFS-DirC-001:PwrAvg
TS2-010RFC:RFS-ADR-001:ItlckStat
TS2-010RFC:RFS-ADR-002:ItlckStat
TS2-010RFC:RFS-ADR-003:ItlckStat
TS2-010RFC:RFS-ADR-004:ItlckStat
TS2-010RFC:RFS-ADR-201004:ItckStat
TS2-010RFC:RFS-DirC-005:PwrFwr
TS2-010RFC:RFS-DirC-005:PwrReflect
TS2-010RFC:RFS-ADR-201005:ItckStat
TS2-010RFC:RFS-DirC-006:PwrFwr
TS2-010RFC:RFS-DirC-006:PwrReflect

## SIM
Slow Interlock Module
I/O | Signal type | Signal name | Pre-cond. Req. | Location | Description | Signal type | Signal name | Property | Description
DO | Dry-contact | TS2-010RFC:RFS-FIM-001:HVena | NA | FIM | HV enable stop command to FIM - HV ON signal output |  | TS2-010RFC:RFS-FIL-001:PSU
DO | Dry-contact | TS2-010RFC:RFS-FIM-001:RFena | NA | FIM | RF enable stop command to FIM - RF ON signal output | AI |  | .I_MON | Current monitoring
AI | 4..20mA | TS2-010RFC:RFS-Main-001:PT | NA | Cooling | Main inlet water pressure (common signal) - no interlock required | AI |  | .W_MON | Watt monitoring
DO | Dry-contact | TS2-010RFC:RFS-DA-001:DAena | NA | DA | Driver amplifier output enable | DI |  | .ON_STAT | ON status
[6 empty] | DI |  | .F_STAT | Fault status
AI | 0..10V | TS2-010RFC:RFS-VacPS-001:I | AUX | IP | Klystron vacuum signal | DI |  | .LOC_REM | Local/Remote status
AI | 0..10V | TS2-010RFC:RFS-VacPS-002:I | AUX | IP | Klystron vacuum signal | AO |  | .I_SET | Current output set-point
DI |  | TS2-010RFC:RFS-Main-001:EmSw | AUX |  | Emergency push button | DO |  | .RST_CMD | Reset command
[6 empty] | DO |  | .ON_CMD | ON command
DI | Dry-contact | TS2-010RFC:RFS-Oil-001:LS | FIL | KLY | Oil tank minimum level switch
DI | Dry-contact | TS2-010RFC:RFS-Oil-001:TSH | FIL | KLY | Oil tank high temperature switch |  | TS2-010RFC:RFS-SolPS-001:PSU
DI | Dry-contact | TS2-010RFC:RFS-Oil-001:LO | FIL | KLY | Oil tank lock open switch | AI |  | .I_MON | Current monitoring
AI | PT100 | TS2-010RFC:RFS-Main-001:TT | FIL | Cooling | Main inlet water temperature (common signal) | AI |  | .V_MON | Voltage monitoring
DI | Dry-contact | TS2-010RFC:RFS-Oil-001:FIS | FIL | Cooling | Oil tank water flow switch | DI |  | .PS_STAT | PSU status
AI | PT100 | TS2-010RFC:RFS-Oil-001:TT | FIL | Cooling | Oil tank outlet water temperature | DO |  | .ENA_STAT | Enable status
AI | PT100 | TS2-010RFC:RFS-Oil-002:TT | FIL | KLY | Oil tank temperature | DO |  | .LOC_REM | Local/Remote status
[6 empty] | AO |  | .I_SET | Current output set-point
DI | Pin-conn | TS2-010RFC:RFS-Kly-001:ES | STDBY | KLY | Klystron cable detection status
DI | Dry-contact | TS2-010RFC:RFS-Kly-001:AS | STDBY | KLY | Klystron airflow switch |  | TS2-010RFC:RFS-SolPS-002:PSU
DI | Dry-contact | TS2-010RFC:RFS-Sol-001:FIS | STDBY | Cooling | Solenoid outlet water flow switch | AI |  | .I_MON | Current monitoring
AI | PT100 | TS2-010RFC:RFS-Sol-001:TT | STDBY | Cooling | Solenoid outlet water temperature | AI |  | .V_MON | Voltage monitoring
AI | 4..20mA | TS2-010RFC:RFS-Coll-001:FIT | STDBY | Cooling | Collector outlet water flow meter | DI |  | .PS_STAT | PSU status
AI | PT100 | TS2-010RFC:RFS-Coll-001:TT | STDBY | Cooling | Collector outlet water temperature | DO |  | .ENA_STAT | Enable status
DI | Dry-contact | TS2-010RFC:RFS-Body-001:FIS | STDBY | Cooling | Body outlet water flow switch | DO |  | .LOC_REM | Local/Remote status
AI | PT100 | TS2-010RFC:RFS-Body-001:TT | STDBY | Cooling | Body outlet water temperature | AO |  | .I_SET | Current output set-point
DI | Dry-contact | TS2-010RFC:RFS-Kly-001:ShldIntact | STDBY | KLY | Klystron shielding intact
NA | VAR_CALC | TS2-010RFC:RFS-Coll-001:SW-CALC | HV ON | PLC | Klystron collector dissipation (Software calculation)
DI | OC | TS2-010RFC:RFS-FIM-001:HVenaStat | HV ON | FIM | HV enable status from FIM (supervision associated)
DI |  | TS2-010RFC:RFS-PSS-001:Ready | HV ON | PSS | PSS permissions ready
DI | Dry-contact | TS2-010RFC:RFS-DA-001:Ready | RF ON | DA | Driver amplifer ready
DI | Dry-contact | TS2-010RFC:RFS-SS-001:OPEN | RF ON | RFDS | RF shutter OPEN - operation mode required
DI | Dry-contact | TS2-010RFC:RFS-SS-001:CLOSE | RF ON | RFDS | RF shutter CLOSE - operation mode required
DI | OC | TS2-010RFC:RFS-FIM-001:RFenaStat | RF ON | FIM | RF enable status from FIM
DI | OC | TS2-010RFC:RFS-ADR-001:CHA | RF ON | RFDS | Arc detector 001-CHA (diagnostic)
DI | OC | TS2-010RFC:RFS-ADR-001:CHB | RF ON | RFDS | Arc detector 001-CHB (diagnostic)
AI | PT100 | TS2-010RFC:RFS-Circ-001:TT | RF ON | Cooling | Circulator outlet water temperature (shared by both Klystrons)
DI | Dry-contact | TS2-010RFC:RFS-Circ-001:FIS | RF ON | Cooling | Circulator outlet water flow switch (shared by both Klystrons)
DI | Dry-contact | TS2-001RFC:RFS-TCU-001:ES | RF ON | RFDS Circ | Circulator TCU ready
AI | PT100 | TS2-010RFC:RFS-Load-001:TT | RF ON | Cooling | Load outlet water temperature
AI | PT100 | TS2-010RFC:RFS-RLoad-001:TT | RF ON | Cooling | Rejected load outlet water temperature
AI | 4..20mA | TS2-010RFC:RFS-RLoad-001:FIT | RF ON | Cooling | Rejected load outlet water flow meter
Channels Req.
DI | 20
DO | 3
AI | 14
Signals which require an internal calculation SIM (VAR_CALC)
Heater PS warm-up time (User parameter) -
Heater PS voltage calculation (PS current and power) – Filament Status required - NOT YET IMPLEMENTED IN THE PLC PROGRAM
Klystron collector dissipation (from flow and DeltaT) – HV Enable : DT = (Toutlet-Tinlet)*FlowMeter
Klystron body dissipation (from flow and DeltaT) – HV Enable : DT = (Toutlet-Tinlet)*FlowMeter - Cannot be calculated without the output flow meter

## FIM
Fast Interlock Module
I/O | Signal type | Signal name | Pre-cond. Req. | Description
DI | Dry contact | TS2-010RFC:RFS-VacPS-001:I-SP | HV ON | Ion-pump1 interlock
DI | Dry contact | TS2-010RFC:RFS-VacPS-002:I-SP | HV ON | Ion-pump2 interlock
DI | 15VDC | TS2-010RFC:RFS-Mod-001:Ready | HV ON | Modulator ready signal
AI | 0..10V | TS2-010RFC:RFS-Mod-001:Cur | HV ON | HV Modulator current waveform - high level (10V = 50A)
AI | 0..10V | TS2-010RFC:RFS-Mod-001:Vol | HV ON | HV Modulator voltage waveform - high level (10V = 110KV)
NA | SW_CALC | TS2-010RFC:RFS-Mod-001:PulseWidth | HV ON | HV Modulator pulse width (source: TS2-010RFC:RFS-Mod-001:Vol )
NA | SW_CALC | TS2-010RFC:RFS-Mod-001:RepRate | HV ON | HV Modulator repetition rate (source: TS2-010RFC:RFS-Mod-001:Vol )
DO | 15VDC | TS2-010RFC:RFS-Mod-001:HvEna | NA | HV enable (inhibit Mod)
DO | 15VDC | TS2-010RFC:RFS-Mod-001:HvEnaInv | NA | HV enable (inhibit Mod) - Spare interved signal
DO | 15VDC | TS2-010RFC:RFS-Mod-001:FastAbort | NA | HV Fast Abort (not used) - Not required by the Modulator
AI | 0..10V | TS2-010RFC:RFS-SolPS-001:Cur | HV ON | Solenoid-01 current interlock
AI | 0..10V | TS2-010RFC:RFS-SolPS-002:Cur | HV ON | Solenoid-02 current interlock
DO | TTL | TS2-010RFC:RFS-PinD-001:RfEna | NA | RF enable (Pin diode) - Fiber optic interface
DO | TTL | TS2-010RFC:RFS-PinD-001:RfEnaInv | NA | RF enable (Pin diode) - Spare inverted signal trhough Fiber-optic
DI | 24VDC | TS2-010RFC:RFS-SIM-001:HvEnaCmd | HV ON | HV enable PLC interlock or sum of interlocks - through PLC dry-contact relay
DO | 24VDC | TS2-010RFC:RFS-SIM-001:RfEnaStat | NA | RF enable PLC status - through optocoupler 24VDC to the PLC
DI | 24VDC | TS2-010RFC:RFS-CAV-001:ChainReady | RF ON | Chain ready (Cavity cryogenic system ready)
DI | 24VDC | TS2-010RFC:RFS-SIM-001:RfEnaCmd | RF ON | RF enable PLC interlock or sum of interlocks - through PLC dry-contact relay
DO | 24VDC | TS2-010RFC:RFS-SIM-001:HvEnaStat | NA | HV enable PLC status - through optocoupler 24VDC to the PLC
AI | +/-10V | TS2-010RFC:RFS-PwrS-110:DaPwrFwd | RF ON | DA power forward (Driver amplifier PwrForw)
DI | TTL | TS2-010RFC:RFS-ADR-201001:ItckStat | RF ON | KLY output arc detector (AFT configuration)
AI | 10Vpp | TS2-010RFC:RFS-DirC-001:PwrFwr | RF ON | DDC1 power forward (output KLY to CIRC)
AI | 10Vpp | TS2-010RFC:RFS-DirC-001:PwrReflect | RF ON | DDC1 power reflecting (output KLY to CIRC)
NA | SW_CALC | TS2-010RFC:RFS-DirC-001:RepRate | RF ON | DDC1 power forward repetition rate
NA | SW_CALC | TS2-010RFC:RFS-DirC-001:PulseWidth | RF ON | DDC1 power forward pulse width
NA | SW_CALC | TS2-010RFC:RFS-DirC-001:PwrAvg | RF ON | DDC1 power forward output average
DI | 24VDC OC | TS2-010RFC:RFS-ADR-001:ItlckStat | RF ON | CIRC arc detector (CERN configuration)
DI | 24VDC OC | TS2-010RFC:RFS-ADR-002:ItlckStat | RF ON | CIRC to LOAD arc detector (CERN configuration)
AI | 10Vpp | TS2-010RFC:RFS-DirC-002:PwrFwr | RF ON | DDC2 power forward (CIRC to LOAD) - not required for interlock
AI | 10Vpp | TS2-010RFC:RFS-DirC-002:PwrReflect | RF ON | DDC2 power reflected (CIRC to LOAD) - not required for interlock
DI | 24VDC OC | TS2-010RFC:RFS-ADR-003:ItlckStat | RF ON | Switch to Hybrid splitter arc detector (CERN configuration)
AI | 10Vpp | TS2-010RFC:RFS-DirC-003:PwrFwr | RF ON | DDC3 power forward (Switch to Hybrid splitter) - not required for interlock
AI | 10Vpp | TS2-010RFC:RFS-DirC-003:PwrReflect | RF ON | DDC3 power reflected (Switch to Hybrid splitter) - not required for interlock
DI | 24VDC OC | TS2-010RFC:RFS-ADR-004:ItlckStat | RF ON | Hybrid splitter to RLoad arc detector (CERN configuration) - No required by HB/MB
AI | 10Vpp | TS2-010RFC:RFS-DirC-004:PwrFwr | RF ON | DDC4 power forward (Hybrid splitter to RLoad) - not required for interlock
AI | 10Vpp | TS2-010RFC:RFS-DirC-004:PwrReflect | RF ON | DDC4 power reflected (Hybrid splitter to RLoad) - not required for interlock
DI | TTL | TS2-010RFC:RFS-ADR-201004:ItckStat | RF ON | Arc detector (AFT configuration) - No required by HB/MB
AI | 10Vpp | TS2-010RFC:RFS-DirC-005:PwrFwr | RF ON | DDC5 power forward (Hybrid splitter to CAV1) - No required by MB/HB
AI | 10Vpp | TS2-010RFC:RFS-DirC-005:PwrReflect | RF ON | DDC5 power reflected (Hybrid splitter to CAV1) - No required by HB/MB
DI | TTL | TS2-010RFC:RFS-ADR-201005:ItckStat | RF ON | Arc detector (AFT configuration)
AI | 10Vpp | TS2-010RFC:RFS-DirC-006:PwrFwr | RF ON | DDC6 power forward (Hybrid splitter to CAV2)
AI | 10Vpp | TS2-010RFC:RFS-DirC-006:PwrReflect | RF ON | DDC6 power reflected (Hybrid splitter to CAV2)
DI | LVDS | TS2-010RFC:RFS-LLRF-001:MonAlarm | RF ON | LLRF monitor alarm
DO | LVDS | TS2-010RFC:RFS-LLRF-001:OutEna | NA | LLRF output enable
*See ARD-DDC sheet for more details
The signal list might vary according to the amplifier configuration
NA - Not applicable for the type of signal
Channels Req.
DI | 14
DO | 8
AI | 17
Signals which require an internal calculation FIM
HV pulse width (from Modulator voltage waveform)
RF pulse width (from RF power detectors)
HV pulse repetition rate (from Modulator voltage waveform)
Version rev.
| 2017.06.13 | Added the signal names

## PLC IO mapping
Sensor type |  |  |  | I/O mapping address
Device type | Signal name | DTYP | Value | Name | Data type | Address
AF_RDATA | TS2-010RFC:RFS-VacPS-001:I | .DTYP := | ISn_IP; | TS2-010RFC:RFS-VacPS-001:I | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-VacPS-001:I | .VAL := | TS2-010RFC:RFS-VacPS-001:I;
AF_RDATA | TS2-010RFC:RFS-VacPS-002:I | .DTYP := | ISn_IP; | TS2-010RFC:RFS-VacPS-002:I | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-VacPS-002:I | .VAL := | TS2-010RFC:RFS-VacPS-002:I;
AF_RDATA | TS2-010RFC:RFS-Main-001:PT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Main-001:PT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Main-001:PT | .VAL := | TS2-010RFC:RFS-Main-001:PT;
AF_RDATA | TS2-010RFC:RFS-Main-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Main-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Main-001:TT | .VAL := | TS2-010RFC:RFS-Main-001:TT;
AF_RDATA | TS2-010RFC:RFS-Oil-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Oil-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Oil-001:TT | .VAL := | TS2-010RFC:RFS-Oil-001:TT;
AF_RDATA | TS2-010RFC:RFS-Oil-002:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Oil-002:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Oil-002:TT | .VAL := | TS2-010RFC:RFS-Oil-002:TT;
AF_RDATA | TS2-010RFC:RFS-Sol-001:FIS | .DTYP := | XXXXXX; | TS2-010RFC:RFS-Sol-001:FIS | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Sol-001:FIS | .VAL := | TS2-010RFC:RFS-Sol-001:FIS;
AF_RDATA | TS2-010RFC:RFS-Sol-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Sol-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Sol-001:TT | .VAL := | TS2-010RFC:RFS-Sol-001:TT;
AF_RDATA | TS2-010RFC:RFS-Coll-001:FIT | .DTYP := | XXXXXX; | TS2-010RFC:RFS-Coll-001:FIT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Coll-001:FIT | .VAL := | TS2-010RFC:RFS-Coll-001:FIT;
AF_RDATA | TS2-010RFC:RFS-Coll-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Coll-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Coll-001:TT | .VAL := | TS2-010RFC:RFS-Coll-001:TT;
AF_RDATA | TS2-010RFC:RFS-Body-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Body-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Body-001:TT | .VAL := | TS2-010RFC:RFS-Body-001:TT;
AF_RDATA | TS2-010RFC:RFS-Circ-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Circ-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Circ-001:TT | .VAL := | TS2-010RFC:RFS-Circ-001:TT;
AF_RDATA | TS2-010RFC:RFS-Load-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-Load-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Load-001:TT | .VAL := | TS2-010RFC:RFS-Load-001:TT;
AF_RDATA | TS2-010RFC:RFS-RLoad-001:TT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-RLoad-001:TT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-RLoad-001:TT | .VAL := | TS2-010RFC:RFS-RLoad-001:TT;
AF_RDATA | TS2-010RFC:RFS-RLoad-001:FIT | .DTYP := | TSn_PT100; | TS2-010RFC:RFS-RLoad-001:FIT | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-RLoad-001:FIT | .VAL := | TS2-010RFC:RFS-RLoad-001:FIT;
AF_RDATA | TS2-010RFC:RFS-Coll-001:SW-CALC | .DTYP := | COLL_DISP; | TS2-010RFC:RFS-Coll-001:SW-CALC | Int | %IWXXX | AF_RDATA | TS2-010RFC:RFS-Coll-001:SW-CALC | .VAL := | TS2-010RFC:RFS-Coll-001:SW-CALC;
DIO_RDATA | TS2-010RFC:RFS-FIM-001:HVena | .DTYP := | "DO"; | TS2-010RFC:RFS-FIM-001:HVena | Bool | %QX.X
DIO_RDATA | TS2-010RFC:RFS-FIM-001:RFena | .DTYP := | "DO"; | TS2-010RFC:RFS-FIM-001:RFena | Bool | %QX.X
DIO_RDATA | TS2-010RFC:RFS-DA-001:Daena | .DTYP := | "DO"; | TS2-010RFC:RFS-DA-001:Daena | Bool | %QX.X
DIO_RDATA | TS2-010RFC:RFS-Main-001:EmSw | .DTYP := | "DI"; | TS2-010RFC:RFS-Main-001:EmSw | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Oil-001:LS | .DTYP := | "DI"; | TS2-010RFC:RFS-Oil-001:LS | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Oil-001:TSH | .DTYP := | "DI"; | TS2-010RFC:RFS-Oil-001:TSH | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Oil-001:LO | .DTYP := | "DI"; | TS2-010RFC:RFS-Oil-001:LO | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Oil-001:FIS | .DTYP := | "DI"; | TS2-010RFC:RFS-Oil-001:FIS | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Kly-001:ES | .DTYP := | "DI"; | TS2-010RFC:RFS-Kly-001:ES | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Kly-001:AS | .DTYP := | "DI"; | TS2-010RFC:RFS-Kly-001:AS | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Body-001:FIS | .DTYP := | "DI"; | TS2-010RFC:RFS-Body-001:FIS | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Kly-001:ShldIntact | .DTYP := | "DI"; | TS2-010RFC:RFS-Kly-001:ShldIntact | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-FIM-001:HVenaStat | .DTYP := | "DI"; | TS2-010RFC:RFS-FIM-001:HVenaStat | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-PSS-001:Ready | .DTYP := | "DI"; | TS2-010RFC:RFS-PSS-001:Ready | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-DA-001:Ready | .DTYP := | "DI"; | TS2-010RFC:RFS-DA-001:Ready | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-SS-001:Shutter | .DTYP := | "DI"; | TS2-010RFC:RFS-SS-001:Shutter | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-FIM-001:RFenaStat | .DTYP := | "DI"; | TS2-010RFC:RFS-FIM-001:RFenaStat | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-ADR-001:CHA | .DTYP := | "DI"; | TS2-010RFC:RFS-ADR-001:CHA | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-ADR-001:CHB | .DTYP := | "DI"; | TS2-010RFC:RFS-ADR-001:CHB | Bool | %IX.X
DIO_RDATA | TS2-010RFC:RFS-Circ-001:FIS | .DTYP := | "DI"; | TS2-010RFC:RFS-Circ-001:FIS | Bool | %IX.X
DIO_RDATA | TS2-001RFC:RFS-TCU-001:ES | .DTYP := | "DI"; | TS2-001RFC:RFS-TCU-001:ES | Bool | %IX.X

## ARD-DDC
Arc detectors and DC in TS-2
| For RF systems |  |  |  | For couplers
|  | AFT AD | CERN AD
Amp | Thales K | CH1 | CH3 (Spare) | Coup-1 | 8-CH, type to be confirmed AFT probably
| CPI K | CH2 | CH4 (Spare)
Coup-2
Circulator | AFT | CH3
| MEGA |  | CH1 | Coup-3
Load | AFT | CH4 |  | Coup-4
| MEGA |  | CH2
Date when required
Reject Load 1 | AFT |  | CH5
Reject Load 2 | AFT |  | CH6 | Phase I |  | June/July 2017
Shutter switch 1 |  |  | CH7 | Phase II |  | Dec 2017 (tbc)
Shutter switch 2 |  |  | CH8
|  |  |  | Phase III |  | Dec 2017 (tbc)
Note- I don't remember whether the AFT load and circulator has CERN AD interfcae pattren. It surely has the AFT AD pattern

## P&ID abbreviation
Name | Meaning
FI | Flow Indicator | Kly | Klystron
FIC | Flow Indicator Controller | Mod | Modulator
FIT | Flow Indicator Transmitter | MO | Signal generator
FS | Flow Switch | LO | LO-box
FIS | Flow Indicator Switch | DirC | Waveguide directional coupler
LS | Level Switch | PwrS | Power Splitter
LO | Lock Open | QueDet | Quench detector
TSH | Temperature Switch [HIGH] | SCU | Analogue, RF
AS | Air Supply | ADS | Optical fiber viewport
ES | Electrical Switch | ADR | Arc detector
ISn | Current sensor
VSn | Voltage sensor
PW | Pulse Width
RP | Repetation Rate
Pwr | Power
Avg | Average
Rep | Repetition
Rate | Rate
Fwd | Forward