## Slide 1: RF Local Protection System RF-LPS Critical Design Review
Rafael Montaño
www.europeanspallationsource.se
17-06-27

## Slide 2
  Interfaces
  Series units
Concepts
Notes: There is a brief summarize about the total system to be installed at ESS

## Slide 3
SIM interfaces
All interfaces related to the interlock signals of the SIM are defined by a hardwired connection. The connectors in the back-plain can also be defined for a specific interface from any of the I/O types of the PLC.
The PLC enclosure design allows the upgradability of the system by adding connectors as required. These connectors then can be connected to the terminal blocks of the PLC A I/O modules.
PLC patch panel connectors
Notes: There is a brief summarize about the total system to be installed at ESS

## Slide 4
SIM interfaces
Klystron sensor connectors
Filament PSU
Solenoid PSU
Temp, flow rate, Pressure, etc.
Ion-pump
IOC
Notes: There is a brief summarize about the total system to be installed at ESS

## Slide 5
PLC Interfaces and I/O protection
Interface | Type of isolation / cable detection
PLC – PSUs | Dry-contacts
PLC – FPGA | Dry-contacts
PLC – Cooling | Secondary power supply
PSUs – PLC | Dry-contacts
Conn. Box – PS-2 | 500 mA fuses
PSUs – PLC | Cable detection
PLC – Sensors | Pull-up/down signals when no sensor connected
PLC – Arc-detector (CERN) | Test arc-detector from a PLC command
The sensors and I/O signals where is required an external power supply (PS) can be powered from a secondary PS, then the CPU and the I/O modules are protected against an external short circuit.

## Slide 6
Series units
Timeline of the series units and system validation
System
received
Connects the system
to the test bench
Automatic
logic validation
System testing and
logic validation
Acceptance test
System report
Notes: There is a brief summarize about the total system to be installed at ESS

## Slide 7
Thanks!!!
Questions