## Slide 1: RF Cell Controls
Timo Korhonen
ICS Chief Engineer
www.europeanspallationsource.se
10 May 2017

## Slide 2: Overview
Overview of RF Cells
Accelerator control concept
  Timing of the machine, mode information
Components
  Status of ICS developments
  Note: PSS and MPS handled in separate talks
Summary

## Slide 3: Information source: RF Cell diagrams
The diagrams provided by RF Group provide the (only available) overview of the systems
These are essential to understand the status of development

## Slide 4: RF Cell setups in ICS understanding
LLRF, RF-LPS (local protection) in all cases
RFQ and DTL
  Modulator, Klystron, (RFQ) tuning with water cooling loops
MEBT
  Solid state amplifier, bunchers, no modulator
Spokes
  RF power with solid state amplifiers, no klystron or modulator
Medium & High Beta
  Modulator, Klystron (MB) or IOT (HB), cryomodules & SC cavities with slow and fast tuners
Walkthrough of integration status of each component

## Slide 5: Components
LLRF
Modulator
Local Protection RF-LPS (and klystron control)
Solid State Amplifier
Circulator Control Unit
Cryomodule
Cavity Control
Vacuum Control (ESS global vacuum controls)
Master Oscillator, phase reference line

## Slide 6: General tasks for ICS
Cell integration
  Controls for each component (EPICS interfaces)
  Global control of the whole cell
Timing system
  Provided for the whole ESS (next slides)
Operating procedures
  Start-up sequences (cell level integration)
  global control interfaces (accelerator level)
Data handling
  Archiving
  Post-mortem
Conditioning procedures
  Have not yet been talked about much
  Require a lot of experience to program well
  Manual conditioning out of question (I assume)

## Slide 7: Timing and machine operation
Machine timing is one of ICS global services
  Short recap of how it works
  More details can be found in ESS-0088633
Drives the operation of the machine
  Close connection to MPS
  Interfaces to many RF components, too.
  Importance is often forgotten
    More than a source of trigger pulses

## Slide 8: Structure of the system
Master Event Generator (EVG) generates a continuous data stream (next slide)
The (accelerator) synchronization frequency (of 88 MHz) will be fed into the master event generator and used as the system clock. Event receivers synchronize to that clock.
The 14 Hz operating frequency will be generated by down conversion from RF in the event generator (divide 88.0525 MHz by 6289464 to get 14.00000064 Hz)
All timing sequences, events, etc., generated in hardware
Master Event Generator
RF Master Oscillator
fanout
Event
receiver
88 MHz
fanout
Event
receiver
Event
receiver
Event
receiver
Event
receiver
Event
receiver
Event
receiver
Event
receiver
Notes: Remember: eye pattern
14 Hz will be generated internally in the EVG. De facto decision.

## Slide 9: Accelerator sequences
Pre-programmed sequences repeat at 14 Hz
  Sequencer with a RF-synchronous 88 MHz clock (can be changed)
  “programming” can happen in less than a millisecond
“Data”, i.e., beam envelope mode, etc., transmitted in parallel
  Contains “plan” for the next cycle: envelope mode, beam/no beam, pulse counter, rep rate,…
  Mode changes require a handshake with BIS
    When mode change is transmitted, timing does not send beam before MPS/BIS gives OK
t
71.4 ms
71.4 ms
71.4 ms
…
DATA
14 Hz <-> 71.4 ms
Modulator, t=0+500 us
RF Pulse, t=0+530 us
Beam On,t=0+535 us
Beam Off, t=0+3395 us
Transmit (well) before next cycle

## Slide 10: LLRF
MTCA-based system
  Hosted in the same MTCA crate with RF-LPS (local protection)
  Heavily dependent on timing (timing receiver in the same crate)
Hardware platforms
  Struck SIS8300-L2 existing, SIS8300-KU new/enhanced version (WIP),
  future IFC1420 (ICS standard platform, in-kind development)

## Slide 11: LLRF integration status (ICS view)
Central control facilities in place
  Development so far oriented for 704 MHz (cold linac)
  EPICS interfaces exist, for cell operation
Discussion needed for
  Warm linac, special configurations (RFQ etc.)
  Interfaces between LPS and LLRF (ICS-relevant ones)
  Tuner handling (motor, piezo; interface details unknown to ICS)
  Concept of machine operation, matching with mode handling, etc.
  “Pulse types” definition (machine level discussion)
  Beam current information to LLRF?
  Feedforwards, learning algorithms
  Archiving, alarms, debugging requirements, data synchronisation

## Slide 12: Modulator
ESS development (SML)
First modulators in-kind from ESS Bilbao
Tendering process ongoing
No ICS interfacing done so far
  Anticipating quite some work in this area
  Good monitoring and system diagnostics would probably be useful
  Strong dependence on timing
Notes: We did NOT agree on the network and streaming interfaces.

## Slide 13: Modulator (SML)
Comments from the PDR (October ’16):
  1) The interface with ICS requirements needs to be finalized prior to release of the request for quote. This should include: HMI, and interlocks connection to the control system. Also the relevant portion of klystron protection shall be well described for the programmers.
    Status: pending
  14) Consider increasing the sampling rate for the analog signal acquisition system. 100 kSa/s may alias important information that may compromise troubleshooting. Consider buffering data locally, storing data files locally after fault events and time-stamping fault events to aid in troubleshooting while equipment is in operation.
    Status: no information
  19) Carefully monitor and manage the software development time schedule.
    Status: (ICS) software development not started. Pending information.
Was briefly discussed but left pending the results of a tender (ESS Bilbao)
  Quite some time has passed since…need urgently to get back to this

## Slide 14: Local Protection (RF-LPS)
Working together with ICS
  PLC part well advanced
  Fast logic part making progress, slowly but surely
    Start has been slow.
    Closing to final specifications and implementation
  Uses ICS standard platform
  Proof-of-concept system, migration towards final MTCA in progress.
Clear interfaces to MPS
Issues to be clarified
  Interoperation with LLRF
  Developments with in-kind partners

## Slide 15: Klystron (RFQ, DTL)
Controls of the klystron are handled in the RF-LPS system
  Solenoid power supply
  Filament heater
  Vacuum pumps
  Cooling
    Blower
    Water temperature, flow
Control system interface (EPICS) is working (in the lab)

## Slide 16: Solid State Amplifier
Klystron pre-amplifier in RFQ, DTL
  Procurement ongoing
  Rough definition of interfaces
    Ethernet-based
    maybe SNMP,SCPI?
  EPICS integration TBD
High power in MEBT
  Details not known (to me)

## Slide 17: Circulator control unit
Some initial ICS work done
  Network interface
  Signal list defined
Pending final hardware

## Slide 18: Cavity control
Work on RFQ controls starting
In-kind with CEA (France)
Details under discussion
Experienced partner, established contacts with ICS

## Slide 19: Cryomodule control
In-kind contribution by IPNO, France
Details becoming clear
EPICS integration by ICS
Integration to the cell control to be discussed

## Slide 20: Master Oscillator, Phase reference line
Good communication with developers
  Details to be clarified but no blocking issues (known).

## Slide 21: Machine-level integration
To be discussed – not much has happened yet
  How to present an integrated view
Interfaces with beam instrumentation
  E.g., beam phase measurement with BPMs
  Feedforwards, role of beam current monitors
Control room operation
  Startup
  Data and control exchange with machine physics applications
Needs still many discussions
  With ICS,RF,BI involvement
  Please do not hesitate to contact us (ICS)

## Slide 22: Summary
Overall picture starts to crystallize
  Still a lot to do with all the interfaces and components
  RF Cell block diagrams have clarified a lot – thank you!
    Saved us a lot of time already
Most urgent issues to address (my view)
  Modulator controls
  Testing of RF-LPS
    Confirm operation of prototype
    Migrate to MTCA (work ongoing)
  Integration of LLRF and RF-LPS
    RF teststand 2
  Clarification of open issues in warm linac