## CERN
|  |  | Rack 1 |  | Total power | 24400 |  |  |  | Rack 2 |  |  | Total power | 10300 |  |  | Rack 3 | Total power | 5400
[5 empty] | Phase | Rating (VA) | [6 empty] | Phase | Rating (VA) |  |  |  | Phase | Rating (VA)
47 | 1U |  | Fan Unit |  |  |  | 47 | 1U |  | Fan Unit |  |  |  |  | 47 | 1U | Fan Unit
46 | [6 empty] | 46 | [7 empty] | 46
45 | 4U |  | AC Power Distribution |  |  |  | 45 | 4U |  | AC Power Distribution |  |  |  |  | 45 | 4U | AC Power Distribution
44 | [6 empty] | 44 | [7 empty] | 44
43 | [6 empty] | 43 | [7 empty] | 43
42 | [6 empty] | 42 | 1U |  | Network switch |  |  |  |  | 42 | 2U | Fast RF Switch | 1 phase | 100
41 | 2U |  | TDK 1 Solenoid supply |  | 3 Phase | 6000 | 41 | [7 empty] | 41
40 | [6 empty] | 40 | 3U |  | TCU and coil power supply |  |  | 1 | 1000 | 40
39 |  |  | Solenoid Contingency |  |  |  | 39 |  |  | CERN: Not needed |  |  |  |  | 39
38 | [6 empty] | 38 | [7 empty] | 38
37 | 2U |  | TDK 2 Solenoid Supply |  | 3 Phase | 6000 | 37 | [7 empty] | 37 |  | CERN Interlock System |  | 1000
36 | [6 empty] | 36 | 10 U |  | Monitor |  |  | 1 Phase | 200 | 36
35 |  |  | Solenoid Contingency |  |  |  | 35 | [7 empty] | 35
34 | [6 empty] | 34 | [7 empty] | 34
33 |  |  | TDK 3 Solenoid Supply |  | 3 Phase | 6000 | 33 | [7 empty] | 33
32 |  |  | (not needed for CERN)) |  |  |  | 32 | [7 empty] | 32
31 |  |  | Solenoid Contingency |  |  |  | 31 | [7 empty] | 31
30 | [6 empty] | 30 | [7 empty] | 30
29 |  | Ion Pump 1 |  | Ion Pump 2 |  |  | 29 | [7 empty] | 29
28 |  | CERN - not in rack |  | CERN - not in rack | 1 Phase | 200 | 28 |  |  | Keyboard |  |  |  |  | 28
27 | [6 empty] | 27 | [7 empty] | 27
26 | [6 empty] | 26 | 6U |  | Space for T&M |  |  |  | 2000 | 26
25 | [6 empty] | 25 |  |  | (eg one oscilloscope |  |  | 1 Phase |  | 25
24 |  |  | Filament Heater Supply |  |  | 1000 | 24 |  |  | One power meter) |  |  | 1 Phase |  | 24
23 | [6 empty] | 23 | [7 empty] | 23
22 | [6 empty] | 22 | [7 empty] | 22
21 | [6 empty] | 21 | [7 empty] | 21
20 | [6 empty] | 20 | [7 empty] | 20
19 | [6 empty] | 19 | 4U |  | Motion Controller |  |  | 1 Phase | 300 | 19
18 |  |  | SSA Driver |  | 1 Phase | 2000 | 18 |  |  | CERN: not needed |  |  |  |  | 18
17 | [6 empty] | 17 | [7 empty] | 17 |  | LLRF MTCA | 1 phase | 1000
16 | [6 empty] | 16 | [7 empty] | 16
15 | [6 empty] | 15 | 4U |  | Piezzo Power Supply |  |  | 1 Phase | 300 | 15
14 | [6 empty] | 14 | [7 empty] | 14
13 |  |  | Air Press Control |  | 1 Phase | 100 | 13 | [7 empty] | 13
12 | [6 empty] | 12 | [7 empty] | 12
11 |  |  | Temp Controller |  | 1 Phase | 100 | 11 | 6U |  | 24 VDC PSU |  |  | 1 Phase | 500 | 11
10 | [6 empty] | 10 | [7 empty] | 10
9 | [6 empty] | 9 | [7 empty] | 9 |  | Local oscillator | 1 Phase | 200
8 |  |  | Patch Panel |  |  |  | 8 | [7 empty] | 8
7 | [6 empty] | 7 | [7 empty] | 7
6 | [6 empty] | 6 | [7 empty] | 6 |  | MPS Interface | 1 Phase | 100
5 | [6 empty] | 5 | 1U |  | Socket strip |  |  | 1 Phase | 3000 | 5
4 |  |  | Extra |  |  | 3000 | 4 |  |  | Extra |  |  |  | 3000 | 4 |  | Extra |  | 3000
3 | [6 empty] | 3 | [7 empty] | 3
2 | [6 empty] | 2 | [7 empty] | 2
1 | [6 empty] | 1 | [7 empty] | 1
[9 empty] | total of all three racks |  | 40100 | VA

## Sheet2
|  |  | Rack 1 | [5 empty] | Rack 2 |  |  |  |  | Rack 3
[5 empty] | Phase | Rating (VA) |  |  |  | Phase | Rating (VA) |  |  |  | Phase | Rating (VA)
47 | 1U |  | Fan Unit |  |  |  | 47 | 1U | Fan Unit |  |  | 47 | 1U | Fan Unit
46 | [6 empty] | 46 |  |  |  |  | 46
45 | 4U |  | AC Power Distribution |  |  |  | 45 | 4U | AC Power Distribution |  |  | 45 | 4U | AC Power Distribution
44 | [6 empty] | 44 |  |  |  |  | 44
43 | [6 empty] | 43 |  |  |  |  | 43
42 | [6 empty] | 42 | 1U | Network switch |  |  | 42 | 2U | Fast RF Switch | 1 phase | 100
41 | 2U |  | TDK 1 Solenoid supply |  | 3 Phase | 6000 | 41 |  |  |  |  | 41
40 | [6 empty] | 40 | 3U | TCU |  |  | 40
39 |  |  | Solenoid Contingency |  |  |  | 39 |  | CERN: Not needed |  |  | 39
38 | [6 empty] | 38 |  |  |  |  | 38
37 | 2U |  | TDK 2 Solenoid Supply |  | 3 Phase | 6000 | 37 |  |  |  |  | 37 |  | CERN Interlock System
36 | [6 empty] | 36 | 10 U | Monitor | 1 Phase | 200 | 36
35 |  |  | Solenoid Contingency |  |  |  | 35 |  |  |  |  | 35
34 | [6 empty] | 34 |  |  |  |  | 34
33 |  |  | TDK 3 Solenoid Supply |  | 3 Phase | 6000 | 33 |  |  |  |  | 33
32 |  |  | (not needed for CERN)) |  |  |  | 32 |  |  |  |  | 32
31 |  |  | Solenoid Contingency |  |  |  | 31 |  |  |  |  | 31
30 | [6 empty] | 30 |  |  |  |  | 30
29 |  | Ion Pump 1 |  | Ion Pump 2 |  |  | 29 |  |  |  |  | 29
28 |  | CERN - not in rack |  | CERN - not in rack | 1 Phase | 200 | 28 |  | Keyboard |  |  | 28
27 | [6 empty] | 27 |  |  |  |  | 27
26 | [6 empty] | 26 | 6U | Space for T&M |  |  | 26
25 | [6 empty] | 25 |  | (eg one oscilloscope | 1 Phase |  | 25
24 |  |  | Filament Heater Supply |  |  |  | 24 |  | One power meter) | 1 Phase |  | 24
23 | [6 empty] | 23 |  |  |  |  | 23
22 | [6 empty] | 22 |  |  |  |  | 22
21 | [6 empty] | 21 |  |  |  |  | 21
20 | [6 empty] | 20 |  |  |  |  | 20
19 | [6 empty] | 19 | 4U | Motion Controller | 1 Phase | 300 | 19
18 |  |  | SSA Driver |  | 1 Phase | 2000 | 18 |  | CERN: not needed |  |  | 18
17 | [6 empty] | 17 |  |  |  |  | 17 |  | LLRF MTCA | 1 phase | 1000
16 | [6 empty] | 16 |  |  |  |  | 16
15 | [6 empty] | 15 | 4U | Piezzo Power Supply | 1 Phase | 300 | 15
14 | [6 empty] | 14 |  |  |  |  | 14
13 |  |  | Air Press Control |  | 1 Phase | 100 | 13 |  |  |  |  | 13
12 | [6 empty] | 12 |  |  |  |  | 12
11 |  |  | Temp Controller |  | 1 Phase | 100 | 11 | 6U | 24 VDC PSU | 1 Phase | 300 | 11
10 | [6 empty] | 10 |  |  |  |  | 10
9 | [6 empty] | 9 |  |  |  |  | 9 |  | Local oscillator | 1 Phase | 200
8 |  |  | Patch Panel |  |  |  | 8 |  |  |  |  | 8
7 | [6 empty] | 7 |  |  |  |  | 7
6 | [6 empty] | 6 |  |  |  |  | 6 |  | MPS Interface | 1 Phase | 100
5 | [6 empty] | 5 | 1U | Socket strip | 1 Phase | 2000 | 5
4 | [6 empty] | 4 |  |  |  |  | 4
3 | [6 empty] | 3 |  |  |  |  | 3
2 | [6 empty] | 2 |  |  |  |  | 2
1 | [6 empty] | 1 |  |  |  |  | 1

## WP8 MB
Instrumentation:
|  | Purpose | Minimum requirement | Range | Accuracy | Alternative (upgrade) | Electrical Interface (signal type) | (Possible instrument tried Good/Bad)
Identifier
| Inlet header pressure relief valve | To prevent exposing devices to excessive pressure. | Value to be agreed and to be compatible with maximum pressure allowed on the header | Protection for excessive header pressure to prevent damage to devices, eg pressure relief valve.
| Outlet header pressure relief valve | To prevent exposing devices to excessive pressure. (Required in case of excessive back pressure) | Value to be agreed and to be compatible with maximum pressure allowed on the header | Protection for excessive header pressure to prevent damage to devices, eg pressure relief valve.
| Inlet Header Pressure indicator | To provide local visual indication of header pressure. Value will be used together with the outlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Inlet header temperature indicator | To indicate, record and interlock on maximum inlet temperature. Value will also be used to determine calorimetric loads (with Tout, and flow); also required to protect devices against excessive inlet temperature. | Temperature sensor, connected to EPICS. Temperature or temperature interlock to be connected to LPS for each RF station. | Operational range | 0.1 deg C | Additional gauge for providing local visibility of the inlet temperature, eg simple temperature gauge
| Outlet header temperature indicator | To indicate, record and interlock on maximum Outlet temperature. | Temperature gauge | Operational range | 1 deg C | Temperature sensor connected to EPICS.
| Flanges for connection of devices | To enable each device to be connected. Blank caps shall be available in case no device is attached.
| Valves | To isolate and/or balance flow for each line. | Manual valve
| Pressure sensor Klystron collector outlet. | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Pressure sensor RF load outlet. | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Pressure sensor Body outlet. | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Pressure sensor Circulator outlet. | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Pressure sensor Solenoid outlet. | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Pressure sensor Gun outlet. | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Pressure sensor Window outlet. * | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Pressure sensor Reject load outlet.* | To provide local visual indication of outlet pressure. Value will be used together with the header inlet pressure to determine pressure drop across devices. | Mechanical gauge; oil filled or vibration damped. | 0-operation pressure; bar gauge; | Visual indicator, eg clock gauge | Electronic transducer, value available via EPICS, accuracy eg 0.1 bar.
| Flow meter Klystron collector outlet. | Interlock and calorimetric | High accuracy, +/- 1%, eg Kone; value used for interlock; interlocking could be via a separate switch, mass flow available via EPICS; local visual | 0-300 l/min | +/- 1% or better
| Flow meter RF load outlet. | Interlock and calorimetric | High accuracy, +/- 1%, eg Kone; value used for interlock; interlocking could be via a separate switch, mass flow available via EPICS; local visual | 0-200 l/min | +/- 1% or better
| Flow meter Body outlet. | Mass flow indication for interlock (essential) and calorimetric data (optional); | Medium accuracy, +/- 10%, value used for interlock; interlocking could be via a separate switch, | 0-30 l/min | +/- 10% or better | Mass flow available via EPICS nice to have
| Flow meter Circulator outlet. | Interlock; calorimetric optional | Medium accuracy, +/- 10%, value used for interlock; interlocking could be via a separate switch, ; local visual | 0-50 l/min | +/- 10% or better | Mass flow available via EPICS nice to have
| Flow meter Solenoid outlet. | Interlock; calorimetric optional | Medium accuracy, +/- 10%, value used for interlock; interlocking could be via a separate switch, ; local visual | 0-30 l/min | +/- 10% or better | Mass flow available via EPICS nice to have
| Flow meter Gun outlet. | Interlock; calorimetric optional | Medium accuracy, +/- 10%, value used for interlock; interlocking could be via a separate switch, ; local visual | 0-30 l/min | +/- 10% or better | Mass flow available via EPICS nice to have
| Flow meter Window outlet. * | Interlock; calorimetric optional | Medium accuracy, +/- 10%, value used for interlock; interlocking could be via a separate switch, ; local visual | 0-30 l/min | +/- 10% or better | Mass flow available via EPICS nice to have
| Flow meter Reject load outlet.* | Interlock and calorimetric | High accuracy, +/- 1%, eg Kone; value used for interlock; interlocking could be via a separate switch, mass flow available via EPICS; local visual | 0-200 l/min | +/- 1% or better | Mass flow available via EPICS nice to have
| Temperature sensor Klystron collector outlet. | Interlock and calorimetric | High accuracy, value used for interlock and calorimetric data; eg PT100; data available via EPICS | min to 80 deg C | +/-1% or better | Local indication preferable.
| Temperature sensor RF load outlet. | Interlock and calorimetric | High accuracy, value used for interlock and calorimetric data; eg PT100; data available via EPICS | min to 80 deg C | +/-1% or better | Local indication preferable.
| Temperature sensor Body outlet. | Interlock and calorimetric | Medium accuracy, value used for interlock; calorimetric data optional; eg PT100; data available via EPICS | min to 80 deg C | +/-5% or better | Local indication preferable. High accuracy = as for collector and load
| Temperature sensor Circulator outlet. | Interlock and calorimetric | Medium accuracy, value used for interlock; calorimetric data optional; eg PT100; data available via EPICS | min to 80 deg C | +/-5% or better | Local indication preferable. High accuracy = as for collector and load
| Temperature sensor Solenoid outlet. | Interlock | Medium accuracy, value used for interlock; calorimetric data optional; eg PT100; data available via EPICS | min to 80 deg C | +/-5% or better | Local indication preferable. High accuracy = as for collector and load
| Temperature sensor Gun outlet. | Interlock | Medium accuracy, value used for interlock; calorimetric data optional; eg PT100; data available via EPICS | min to 80 deg C | +/-5% or better | Local indication preferable. High accuracy = as for collector and load
| Temperature sensor Window outlet. * | Interlock | Medium accuracy, value used for interlock; calorimetric data optional; eg PT100; data available via EPICS | min to 80 deg C | +/-5% or better | Local indication preferable. High accuracy = as for collector and load
| Temperature sensor Reject load outlet.* | Interlock | Medium accuracy, value used for interlock; calorimetric data optional; eg PT100; data available via EPICS | min to 80 deg C | +/-5% or better | Local indication preferable. High accuracy = as for collector and load
By Pass
1
FM-FS
P
T
P
T
FM-FS
P
T
FM-FS
P
T
FM-FS
P
T
FM-FS
P
T
2
P
3
P
4
P
5
P
6
P
FM-FS
P
T
P
P
FM-FS
P
T
FM-FS
P
T
7
8
Drain
By Pass
Blank flanges
Body 1
Collector
Output Window
Oil Tank
Body 2 /Electromagnet
Circulator (when required)
RF Load
Spare
1
RF Load
Not Required by placing load and collector in series
Sized for up to 300 l/min
Sized for up to 5 0l/min
Sized for up to 50 l/min
Sized for up to 50 l/min
Sized for up to 50 l/min
Sized for up to 50 l/min
Sized for up to 300 l/min