## Coversheet
[6 empty] | Document No.: | ESS-
|  | HAZOP RECORD SHEET |  |  |  | Project No.: | WP16
ESS WP16
List of HAZOP Participants
Name |  |  |  | Position |  |  | Attendance Date
Duy | Phan
Anton | Lundmark
Akif | Coku
Attachments
Revisions
X | 2
1
Status | Revision | Date | Description |  | Issued | Approved | Released

## HAZOP protocol
Components | LINAC systems include: RF amplifiers (klystrons, tetrodes, solid state amplifiers (MEBT)) RFDS components, i.e. circulator, isolation loads, reject loads Power converters, i.e modulators, Rack air handling units Rack handling units are located on CWL (8 °C circuit) Circulator, spoke loads, klystron oil tank, body and electromagnet, spoke power station (except anode), MEBT SS amplifiers are located on CWM (25 °C) circuit Klystron collectors, tetrode anodes, and RF loads (except spoke) are located on CWH (50 °C) circuit RF gallery systems are supplied with cooling water via three G02 process substations (low beta substation, medium beta substation, high beta substation) There are no subsystems for G02 RF gallery, i.e. the cooling water is directly suplied from central processing plant. CWH circuit has shunt pumps in order to allow for increased temperaure, i.e. for heat recovery purposes Local cooling system is defined as the piping between main supply (CF) up to the LINAC systems, i.e. scope of WP16.
Number | Key word | Deviation | Possible causes |  | Consequences for LINAC systems | Existing safeguards |  | Comments & recommendations
|  |  | central processing plant | Local cooling system |  | central processing plant | on the LINAC systems
1 | flow | high | - Malfunction of pumps - failure of the pump control system - malfunction of flow meters |  | - Cooling performance of the system increased - Induced mechanical vibrations | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (flow meters, pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
2 |  | low | - Malfunction of pumps - Malfunction of flow meters - failure of the pump control system (PLC, VFD, etc) - leak(s) in cooling circuit | leaks in ooling circuit | - Cooling performance of the system decreased. - Overheating of the LINAC systems | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (flow meters, pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
3 |  | zero | - Malfunction of pumps - Malfunction of flow meters - failure of the pump control system (PLC, VFD, etc) - leak(s) in cooling circuit | Major leak in cooling system | Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (flow meters, pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
4 |  | unstable | - Malfunction CUB pumps - leak(s) in cooling circuit |  | - Cooling performance of the system decreased. - Overheating of the LINAC systems | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (flow meters, pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
5 |  | reverse | - Unexpected closing of the pneumatic valves (e.g. V009, V012) due to loss of instrument air - Unexpected closing of gate valves (e.g. V011, V010, V019) |  | - Overheating of the LINAC systems (e.g. RF couplers, quadrupole magnets) - erroneous flow switch signal | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (flow meters, pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
6 | pressure | high | - malfunction of the pumps - failure of the pump control system |  | potential damage of the LINAC systems | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
7 |  | low | - Malfunction of the pump - leak(s) in cooling circuit - malfunction of one of pressure sensors for pump control |  | - cooling performance of the system decreased - overheating of the LINAC systems | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
8 |  | zero | - Pump failure - failure of the pump control system (VFD, PLC, etc) - Electrical power cut - leak(s) in cooling circuit |  | overheating of the LINAC systems | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
9 |  | unstable | - Malfunction of the pump - leak(s) in cooling circuit |  | - Cooling performance of the system decreased. - Overheating of the LINAC systems | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundancy of pumps - redundant sensors (pressure sensors) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
10 | temperature | high | - loss of heat sink (district heating, back-up cooler, etc) - malfunction of temperature sensors - wrong set point defined by the operator |  | - Cooling performance of the system decreased. - Overheating of the LINAC systems | Redundant heat sinks - alarms (e.g. high temperature, instrument error) | Flow meters and pressure gauges on all components | procurement of central prosessing plant is onging Details are TBD
11 |  | low | malfunction of temperature sensors - wrong set point defined by the operator |  | general no impact unless so low so that the water condenses | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundant sensors | temperature sensors downstream some LINAC systems | procurement of central prosessing plant is onging Details are TBD
12 |  | unstable | malfunction of temperature sensors or temperaure control |  | - Poor cooling performance of LINAC systems - Poor operation due to tuning of Klystron body circuit (CWM) | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundant sensors | temperature sensors downstream some LINAC systems | procurement of central prosessing plant is onging Details are TBD
13 | water quality | low (high conductivity, particles) | - failure of skid deminineralizer - corrosion in pipes - filters clogged - pump failure | corrosion in pipes and components LINAC systems poorly cleaned before connection to main water supply | - errosion, cloggin -> low flow through component - lower lifetime - failure of tetrodes and modulators due to poor conductivity | Details are TBD but expected safeguards are: 'alarms (e.g. pump error, PLC error, instrument error) - redundant sensors |  | procurement of central prosessing plant is onging Details are TBD
14 | corrosion | excessive | - poor maintenance - poor corrosion protection - inadequate selection of materials - long term failure of the degassing unit | - poor maintenance - poor corrosion protection - inadequate selection of materials | cooling performance of the system decreased reduced lifetime | - stainless steel pipes - degassing unit - regular maintenace and inspection |  | procurement of central prosessing plant is onging Details are TBD
15 | mechanical vibration | excessive | - pump control failure - pump failure - poor mechanical design of support systems | high flow velocities poor mechanical design of support systems | break of LINAC systems reduced lifetime of LINAC systems | Design according to code Design according to best practicies requirements on pump/shaft aligment Pump frequency monitoring | Design according to code Design according to best practicies | procurement of central prosessing plant is onging Details are TBD
16 | loss of confinement |  | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves | - failure of hoses, joints, flanges, gaskets - inadvertent opening of certain valves | Leaks in cooling circuits low or no coolant flow hazards for operators/technicians | Design according to code Design according to best practicies Use of proper materials | Design according to code Design according to best practicies Use of proper materials | procurement of central prosessing plant is onging Details are TBD
17 | release of activated water | uncontrolled | N/A |  |  |  |  | procurement of central prosessing plant is onging Details are TBD
18 | contact with hot surfaces |  | maintenance of equipment | maintenance of equipment | Hazards for operators/technicians | insluated surfaces T>50 °C | insluated surfaces T>50 °C | procurement of central prosessing plant is onging Details are TBD