## Slide 1: Controls Infrastructure
Timo Korhonen
ICS Chief Engineer
www.europeanspallationsource.se
21 May 2017

## Slide 2: Overview
Control system infrastructure components
MTCA base infrastructure
Timing system
Machine Protection System
Digital platforms, status and support
Procurement and Installation
Interface with Beam Instrumentation
Summary

## Slide 3: Control system infrastructure components
MTCA.4
  Crates, MCH, Cooling Units, PSU
  Platform Management
  Crate variants: 12-slot and 6-slot
I/O and processing
  Digital platforms
Network and servers
  Network hardware in-kind contribution from Norway
Timing System
  EVG, EVR, Distribution System

## Slide 4: MTCA base infrastructure
Crates in two variants
12-slot, 9U crate
  For (LL)RF systems that can utilize many slots
  Has been in use, stable configuration
6-slot, 3U crate
  For smaller, more distributed systems (saves rack space)
  Backplane issues
    Vendors consider MTCA backplanes as “custom”
    Defined an “ESS-specific” backplane – follows layout of the bigger crate
  Cooling and airflow issues with prototype
    Added one fan to improve airflow
    Front-to-rear cooling is challenging due to small air inlet area
MCH (Micro Channel Hub) standardized on N.A.T.
Power supplies need final definition
  Wiener has good noise performance but issues with size

## Slide 5: MTCA Crate variants
3U, 6-slot crate
4 slots with place for rear transition module
CPU, EVR in remaining slots
9U, 12-slot crate
12 slots with place for rear transition module
2 MCH slots (redundancy)
4 PSU slots (2 with double width, e.g. WIENER)

## Slide 6: Timing system
MRF Event System
  Components defined
  Uses latest design with active delay compensation
    Higher frame rate possible
    Unlimited fan-out depth
    Etc.
  MTCA.4 version with backplane trigger and clock support
    Software support to be finalized
Details of interfacing to BI (and other) systems to be discussed and finalized
  A preliminary, incomplete definition exists (ESS-0088633)

## Slide 7: Machine Protection System
Interfacing to MPS
  System concept is ready and accepted
  Detail discussions are still underway
Interface defined, consisting of
  Discrete lines
    OK/NOK, disconnect (“3-wire”)
    For fast switch-off
  Ethernet link (UDP)
    Operating mode checking, heartbeat, online testing
    Removes dependency on timing system direct link for mode data transfer
      PDR recommendation was to investigate this issue

## Slide 8: Digital platforms, status and support
Struck SIS8300-L2,KU
  Supported until final platform (IFC1420) at equivalent or better performance level
    The agreement as I have understood it.
    We assume that this system is essentially ready (no substantial development resources needed.)
  MPS (BIS) interface issues to be clarified
    ESS-designed interface cannot be used (no compatible outputs)
    “collect” signals from different connectors (Harlink, RTM, SFP)
    Firmware interface (programming resources to be found)
  Procurement etc. is BI responsibility

## Slide 9: IFC1420
Consists of a FMC carrier (IFC1411) and a mezzanine ADC module (IFC1430) (can be replaced)
  10 Ch ADC (TI ADS42LB69, 250 MSPS, 16 bits)
  4 CH DAC (TI DAC38J84, 2.5 GSPS, 16 bits)
Two standard (HPC) FMC slots (one usually used for 1430)
In IFC1420 configuration, front plate space can still be used for a BIS (Beam Interlock System) mezzanine
  One FMC slot still remains free for use (SFP, additional ADCs, DI/O, …)
Other specifications like the already existing IFC1410, with minor changes
  Mostly due to digital vs. analog RTM interface
  Firmware, software essentially the same (some differences due to signal routing etc.)

## Slide 10: IFC1420 layout overview
BIS special
mezzanine
ADC Mezzanine (1430)
FMC slot #1
FMC slot #2
Notes: IFC1411 can be used with two FMCs! (i.e., both FMC slots are forward-facing)

## Slide 11: Digital platforms, status and support
IFC1420
  Delays due to slow start of in-kind
    And ramp-up of internal resources
    On the other hand, too early design would have meant rework.
  CDR on Wednesday (May 23), prototype production scheduled for June
    Unless major obstacles show up in CDR
  Strong support from PSI (in-kind)
    1 FPGA engineer, 1 SW engineer full time, 2 more will be employed
    Part-time support of 7 more people (controls, LLRF, instrumentation)
    Use of PSI resources for analog characterization (in progress)
    Frees up internal staff for integration tasks
  Hardware also contributed in-kind

## Slide 12: Preliminary results (same ADCs on a FMC)
Clock signal generated with an IFR2042 signal generator and filtered by four cascaded Mini-circuits filters. The IF signal is generated with and ROHDE&SCHWARZ SMA200 signal generator and filtered by two cascaded Mini-circuits filters.
Data from ADC is acquired and analysed with Matlab scripts.
Measurements can be easily reproduced. Exact specifications of frequencies of interest, etc. are required. These measurements are with SwissFEL LLRF parameters.
Not to be quoted – system in set-up
Definitive results coming soon.

## Slide 13: Networks and servers
Network design done
  Technical (aka controls) network backbone
  State-of-the-art performance level
  Hardware in-kind contribution from Norway
  Installation, cabling is underway
    System-level connection details to be defined
Some EPICS IOCs already running on site
  CF systems with PLCs
Temporary control room being equipped
  As well as server infrastructure (also temporary until server room ready)

## Slide 14: Procurement and Installation
3U Crate expected in June (new backplane, “custom”)
  No agreed “standard backplane” by the manufacturers (according to our discussions)
9U crate technically ready
Need to go through a tendering process (3U and 9U)
  Resulting in a framework agreement
  Final delivery timetable to be defined
Timing system components procurement in progress
  Backbone cabling design done, detail distribution TBD
IFC1420 from in-kind partner as soon as FAR (final Article Review) done + procurement time
  Need to decide how many and when

## Slide 15: Interface with Beam Instrumentation
From our latest ICD document (should be updated and finalized)
MPS/BIS interface missing
Discussion on data interfaces (EPICS PVs, to beam physics, etc. to be done)
Work on defining requirements for archiving and other services necessary
Data management, calibration, operating procedures to be discussed in detail.

## Slide 16: Summary
MTCA base infrastructure defined
  Work still required to verify performance and functionality
Timing system components defined
  Procurement process in preparation
Platform support defined
  Details still to be finalized
  Final platform development speeding up after a slow start
Control system services defined but more details to be discussed
  Interface document should be finalized