## Slide 1: LLRF for RF review 11-12 May 2017
Anders J Johansson
Lund University
v.1.1

## Slide 2: LLRF functionality
The algorithms and functions should
  Control the cavity field during the pulses
  Tune the cavity by the slow tuners
  Control the fast tuners
  Support the procedures developed with the necessary functionality.

## Slide 3: Cavity field regulation accuracy
 | Frequency (MHz) | Phase accuracy (RMS) | Amplitude accuracy (RMS)
RFQ | 352.21 | 0.2 deg | 0.2 %
Buncher | 352.21 | 0.2 deg | 0.2 %
DTL Static dynamic | 352.21 | 0.2 deg | 0.2 %
Spoke | 352.21 | 0.1 deg | 0.1 %
Medium-Beta | 704.42 | 0.1 deg | 0.1 %
High-Beta | 704.42 | 0.1 deg | 0.1 %
RMS values for time duration of beam, excluding the initial 10 us. In addition, the permissible drift of the phase between two adjacent cavities is 0.1 degrees, with a maximum of 1 degree between any two cavities along the accelerator.

## Slide 4: LLRF system : General view
Klystron HV
Beam current

## Slide 5: High level LLRF architecture
Procedures
  Schemes that involves longer times and multiple pulses.
Algorithms
  Updates that takes place between pulses (68 ms).
Functions
  Real-time control within a pulse (3.5 ms).
Functions
Firmware
Algorithms
Software
Procedures
Scripts
EPICS
PCIe
FPGA
CPU
CPU
LLRF

## Slide 6: Timing and Phase Reference
MRF timing system in gallery distributes triggers.
Phase reference line in tunnel.

## Slide 7
FPGA/ADC
PZ
FPGA
CPU
Timing
Timing
MCH
EPICS, Supervision
Modulator voltage
Spare
Vectormodulator out
Piezo 1
Piezo 2
Monitor
Phase referense
Cavity Pickup
VM out
PreAmp Out
PowerAmp out
PowerAmp Refl
Cavity In
Cavity Refl
Fan Tray x 2
PSU x 2
Interlock
352.21 MHz MTCA.4 example - Spoke
CB control on backplane
Timing triggers
MCH supervision
External I/O
Ethernet on backplane
230 V AC
Phase referense
Cavity Pickup
VM out
PreAmp Out
PowerAmp out
PowerAmp Refl
Cavity In
Cavity Refl
Phase referense
Cavity Pickup
VM out
PreAmp Out
PowerAmp out
PowerAmp Refl
Cavity In
Cavity Refl
LO-generation
LO/REF
RF/VM
352 MHz
Updated
Updated
In-Kind
In-Kind
In-Kind

## Slide 8
HW: RTM-Digitizer
5*2 ADCs
Kintex
Ultrascale
FPGA
2GB DDR3
Zone3
connector
Backplane connector
Optical interface
Attenuators downconverters
Vector modulator
2*DC-signal
input
8*AC-signal
input
DAC
Vector
modulator
output

## Slide 9: Slow tuner control
The slow tuner control will be done with the ESS standard motion controller: a Beckhoff solution controlled over EPICS by EtherCat.

## Slide 10: ESS LLRF WU
ESS Eric and Lund University
  Responsible for overall LLRF system design and performance.
  Develop control algorithms and functions for cavity field control, fast and slow tuning.
  Implement these in the firmware (FPGA) and software (CPU).
  Monitor the activities of the in-kind partners.
  Owner of the LLRF system during operations (ESS Eric).

## Slide 11: In-kind contributions
PEG
  Develop LO-generator MTCA board
  Develop Pz-control MTCA board
  Develop RTM carrier MTCA board
  Develop cavity simulator for test and commissioning
  Assemble, configure, test and deliver LLRF systems for the 704 MHz Linac.
ESS Bilbao
  Develop LO generator for 352 MHz linac.
  Adopt the LLRF firmware for multiple pickups at DTLs.
  Adopt the LLRF firmware for the multiple pickups at RFQ.
  Procure, assemble, configure, test and deliver LLRF systems for the 352 MHz Linac.

## Slide 12: LLRF control within a pulse. (Baseband model)
PID
PID
Feed-forward table
+
Cavity
Setpoint
-
Ripple Model
BCM
Ripple Model
Modulator
HV
FPGA

## Slide 13: Functions (Firmware in FPGA)
Operation Mode | Usage
PI-driven loop | Output is driven by the PI-control and the feed-forward table is added as a delta signal.
FF-driven loop | Output is driven by the feed-forward table and the PI-control is used to control the remaining error.
IQ signal generator | Open loop mode, where the set-point and feed-forward tables are used to create an output wave form, specified in IQ-points.
Magnitude-phase signal generator | Open loop mode, where the set-point and feed-forward tables are used to create an output wave form, specified in magnitude and phase.
Frequency-offset | Open loop mode, where magnitude is fixed and phase is increasing or decreasing. This creates an output with a frequency that is above or below the nominal RF frequency of 352.21 or 704.42 MHz

## Slide 14
LLRF FPGA
Iterative Learning Algorithm
LLRF
Feed-forward table
Piezo FPGA
Piezo Feedforward table
Cavity field, Pfwd, Prefl
Detuning calculation
Stepper motor controller
Tuning adjustment
Control room controls
EPICS
CPU
Control room displays
PVs
Reference settings
LLRF control between pulses.
(Iterative Learning Algorithm)

## Slide 15: Algorithms (In CPU)
Algortihm | Description
PI-tuning | Performs a search for optimal PI controller parameters.
Ripple filter tuning | Performs a search for optimal ripple filter parameters.
Notch filter tuning | Performs a search for optimal notch filter parameters.
Feedforward table update (iterative learning control - ILC) | Updates the feedforward correction table based on the measurements on the previous pulses.
Piezo waveform update | Computes a new piezo excitation waveform based on the measurements from the cavity.*
Piezo relaxation | Adjusts the static (DC) component of the piezo waveform by tuning the cavity by the slow tuner.*
Cavity tune calculation | Calculates the Q and tune of the cavity using measurements from the last pulse.

## Slide 16
LLRF FPGA
PI-tuning
Ripple/Notch filter tuning
Piezo FPGA
System identification
Cavity field, Pfwd, Prefl
Detuning calculation
Stepper motor controller
Tuning adjustment
Control room controls
EPICS
CPU
Control room displays
PVs
Reference settings
LLRF control setup.

## Slide 17: Closed loop LLRF tests and verification
Cavity | Frequency | Site | Date (V1/V2)
Pill box | 352 MHz | Lund University | Done/Q3-17
Pill box | 704 MHz | Lund University | Done/Q3-17
Spoke | 352 MHz | Freia, Uppsala | Q4-17
Elliptical | 704 MHz | Saclay, Paris | Q4-17
Elliptical | 704 MHz | Test stand 2, ESS | TBD
Buncher | 352 MHz | Bilbao | Q3-17
RFQ | 352 MHz | ESS On-site | TBD
DTL | 352 MHz | ESS On-site | TBD

## Slide 18: Three (four) LLRF systems running today.
352 MHz LLRF system Freia test hall Uppsala University
352 MHz LLRF test bench Lund University
704 MHz LLRF test bench Lund University
(Under revision)
Additional test stands under
development:
NCBJ – Swierk, Poland
DMCS – Lodz, Poland
ISE – Warsaw, Poland
ESS Bilbao - Spain
Test stand 2 – ESS, Lund