## Slide 1: Conventional Facilities General update D&E buildings Experimental Halls and galleries
Antonio Bianchi
NSS Installation Co-ordinator
European Spallation Source ERIC
www.europeanspallationsource.se
27th September 2017

## Slide 2: CF scope of work
Conventional Facilities (CF) works to prepare and execute the construction of European Spallation Source ERIC. Responsibilities include all buildings and systems required for operation of Accelerator, Target and Instruments, as well as site and infrastructure preparation, construction support, all facility buildings, user and general service buildings.
With reference to NSS Division, the buildings to be delivered are the following:
Building | Description | Delivery date (FULL ACCESS) | Building access
D01 | Experimental Hall (Hall n. 1) | 28.06.2020 | Partial Access according to the Master Schedule 3.4
D03 | Experimental (Hall n. 2) | 02.04.2020 | Partial Access according to the Master Schedule 3.4
D04 | Laboratory & Workshops | 18.08.2019 | 
D07 | Laboratory & Workshops | 19.12.2019 Out of CF Scope | CF provides design (18 months later)
D08 | Laboratory & Workshops | 19.12.2019 | tbd
E01 | Experimental Hall (Hall n. 3) | 27.04.2019 | Partial Access according to the Master Schedule 3.4
E02 | Instruments Guide Hall | 19.12.2019 | Partial Access according to the Master Schedule 3.4
E03 | Laboratory & Workshops | 27.04.2019 | January 2019 (furnishing for sample preparation area)
E04 | Laboratory & Workshops | 27.04.2019 | tbd

## Slide 3: Access Dates for NSS IK partners
E02
E03
E04
E05
E01
D06
D07
D08
1b
4
3
2
1a
2
E01 – Full Access 27-May-19 (incl. Crane)
1a
1b
E02 Area 1 – Partial Access 27-May-19
E02 Area 2 – Partial Access 15-Nov-19
D03 Main Hall – Partial Access 01-Dec-19 (incl. Cranes)
3
D01 Area 1 Main Hall – Partial Access 06-Feb-20
(incl. Cranes)
4
D01 Area 2 Main Hall – Partial Access 02-April-20
(incl. Crane)
5
Exact Location of Final De-Lineation Point TBC
5
D01
D03
D02
D05
D04
Hand-over dates from NSS Project to Instrument teams
RML to be completed before B.o.T.
Out of CF scope
Delivered from NSS ( April 2021)
D04 Full access
18.08.2019
D08 Full access
19.12.2019
E03, E04
Full access
27.04.2019

## Slide 4: E01-E05 3-Month Lookahead

## Slide 5: E-buildings are going up NOW!
E01, E03, E04:
full access April 2019
Sample prep labs:
furnishing to commence January 2019

## Slide 6: D&E buildings - slabs load capacity
10 ton capacity
ALL AREAS

## Slide 7
Gallery Penetrations (D03)
Penetration position to be marked from C.F.
Conduits
Areas suitable for penetrations
Penetrations not allowed

## Slide 8: Logistics

## Slide 9: E02 Beam support concept design
Slab/pile joint
From Gabor Laslo

## Slide 10: Load test E01 – Technical report
Beam over the piles row
1
2
2
1

## Slide 11: Load test design
1st step
2nd step
3rd step
Laser tracker
Laser tracker
Measured points

## Slide 12: Load test E01 – August/September 2017
Little gap to measure inside
Section view

## Slide 13: Load test: final result
Date | Epoch | Load (T/m2) | Comments | Deflection (mm) | Comments
17/08/2017 | 0 | No Load (only 2 beams) | Zero status | 0,0000 | Initial Measurement – No load - only 2 beams
22/08/2017 | 1 | 8.6 T/m2 | 20 hours after loading | 0,3204 | 8.6 T/m2 - 20 hours after loading
22/08/2017 | 2 | 16.3 T/m2 | 3 hours after loading | 0,2396 | 16.3 T/m2 - 3 hours after loading
23/08/2017 | 3 | 24 T/m2 | 4 hours after loading | 0,3388 | 24 T/m2 - 4 hours after loading
30/08/2017 | 4 | 24 T/m2 | 7 days after loading | 0,3760 | 24 T/m2 – 7 days after loading
05/09/2017 | 5 | 24 T/m2 | 13 days after loading | 0,5484 | 24 T/m2 – 13 days after loading
15/09/2017 | 6 | 24 T/m2 | 23 days after loading | 0,7103 | 24 T/m2 –23 days after loading
22/09/2017 | 7 | 4 days after NO LOAD | 4 days after NO LOAD | 0,5539 | 4 days after NO LOAD
NSS requirement: 3+3 mm (3 mm elastic + 3 mm plastic)
Final total deflection: 0,71 mm

## Slide 14: Deformation diagrams
Epoch 1 : 8.6 t/m2 20 hours after loading
  Epoch 2: 16.3 T/m2 - 3 hours after loading
  Epoch 3: 24 T/m2 - 4 hours after loading
  0,3204 mm
  0,2396 mm
  0,3388 mm

## Slide 15: Deformation diagrams
  Epoch 4 : 24 T/m2 – 7 days after loading
  Epoch 5: 24 T/m2 – 13 days after loading
  Epoch 6: 24 T/m2 – 23 days after loading
  0,3760 mm
  0,5484 mm
  0,7103 mm

## Slide 16: Deformation diagrams
  Epoch 7: 4 days after NO LOAD
  Further information available on Chess
  ESS - 0134619
  0,5539 mm
  Comment
  The concrete slab behaviour into E01 fulfil the NSS requirement and the total deflection surveyed is consistent with the structural analysis.
  A single month load test provides an indication but remain a partial results on the slab behavior.

## Slide 17: Naviswork - 3D coordination models
Updated coordination model D buildings | ESS-0026363 (available in CHESS)
Updated coordination model E buildings | ESS-0026362 (available in CHESS)
You can download Navisworks Freedom 2017 at: http://www.autodesk.com/products/autodesk-navisworks-family/autodesk-navisworks-freedom

## Slide 18: Naviswork 3D model (E01,E02,D03 buildings)
Buildings and instruments integration

## Slide 19: Sections E buildings

## Slide 20: Questions