## Slide 1: Ion Source IRR – WP16
Anton Lundmark
Cooling System Engineer
www.europeanspallationsource.se
4 September 2017

## Slide 2: Outline
CF design parameters
Cooling skid
System P&ID
Pipe routing
Upcoming work

## Slide 3: Prerequisites – CF process design parameters

## Slide 4: Cooling skid for IS
CWL-CWS01 provided by WP16
  IS/LEBT/MEBT/DTL FC
  Nominal flow rate: 16 – 20 m3/h
  Nominal heat load: 75 – 85 kW
  Nominal pressure drop: 5.5 – 6.5 bar
  Design temperature: 50 °C
  Design pressure: 10 bar(g)
  Nominal operating temperature: 20 +/-5 °C
  Water Conductivity: 1 μS/cm

## Slide 5: P&ID

## Slide 6: G01 accelerator tunnel

## Slide 7: Pipe routing

## Slide 8: Instrument air for IS/LEBT
No requirements transmitted to previous integration team, however we guess we need something
CF has installed header in tunnel roof with “fixed” capacity
WP16 will locate air manifold by IS/LEBT
  Number of outlets?
  Size? 3 mm hoses?

## Slide 9: Instrument air for NCL
Location of manifolds?
Number and size of outlets?

## Slide 10: IA for IS/LEBT

## Slide 11: Ongoing and upcoming tasks to support IS installation and commissioning
Install tunnel piping and cable trays
Install and commission water skid – G.R.E (UK)
Design and install instrument air manifold
Design and install water pipes for FEB racks
Open issues;
  Pressure reducer for Iris
  Connection of Catania manifolds
  Required documentation before connection – design documents, etc.