## First page
ODH Phase 1 Hazard Register
| Name | Role/Title | Issue date | Revision
Owner | Stuart Birch | Senior Engineer, Personnel Safety Systems | 15th September 2017 | v 2.0
Reviewer | Denis Paulic Duy Phan Bertil Winer
Approver | Ralf Trant

## Instructions
Overall PSS relevant Hazards | Brief description
Hazard ID | ODH_Hazard_xxx - ODH relevant hazard ID are created to be consistent throughout this sheet and reports.
Hazard | In total 2 hazards are identified which are ODH relevant.
Hazard Description | Hazard description is provided to the respective ODH hazard.
PSS1 Hazard | Only 2 hazards are ODH relevant, which are considered in ODH Hazard Register.
Remarks | Remarks are added.
ODH Hazard Register | Brief description
Hazard ID | ODH_Hazard_xxx - PSS relevant hazard ID are created to be consistent throughout this sheet and reports.
Hazard/Top Event | Only 2 hazards are ODH relevant are considered as top event and associated initiating events are identified.
Area | Defines the area in which the hazard can occur
Initiating Event | ODH initiating events are identified leading to specific ODH hazard.
Quantity | Quantity of devices in the area where the hazard can occur
ODH Classification | Classification determined by Acceleration Division
Classification Remarks | Specific classifucation remarks
Consequence | Consequence from Hazard
Likelihood for a particular device | Likelihood for a single device
Likelihood | Likelihood for the total number of devices in an area
Area Occupation | Number of personnel within an area at any time (both normal operation and maintenance)
Barriers and procedures | A list of ODH barriers and procedures that are in place to detect the initiating event
Detection and mittigation | A list of ODH detection and mitigation.
Monitors | Number of ODH detection monitors in an area
Human Actions | A list of Human Action associated with the initiating event and ODH functions.
Risk Measures independent of PSS | Other risk measures independent to PSS but implemented in ESS overall design.

## Overall ODH relevant Hazards
Hazard ID | Hazard | Hazard Description
PSS_ODH Hazard_001 | Oxygen deficiency hazard from Helium | Catastrophic failures of devices (valves, flanges pipe etc.) leading to a large inventroy of helium entering areas were personnel will be carrying out checks and maintenance or personnel enter an area which has a larger nventroy of Helium in that area
PSS_ODH Hazard_002 | Oxygen deficiency hazard from Nitrogen | Catastrophic failures of devices (valves, flanges pipe etc.) leading to a large inventory of Nitrogen entering areas were personnel will be carrying out checks and maintenance or personnel enter an area which has a large inventory of Nitrogen in that area

## ODH Hazard Register
ODH Hazard ID | Hazard | Area | Initiating Event | Quantity | ODH Classification | Classification remarks | Consequence | Likelihood (Frequency/event/hour) per unit | Likelihood (Frequency/event/hour) total | Area occupation | Barriers and procedures | Protection and Mitigation | Monitors | Human Actions | Risk Measures independent of ODH Detection system
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a pipe flange causes a large inventory of helium to leaks into the area. | Failure of pipe flanges (23 off in the ACCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | 2.3e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards) |  | 2.159
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a safety relief device causes a large inventory of helium to leak into the area | Failure of safety relief devices (8 off in the ACCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 4e-09 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a valve causes a large inventory of helium to leak into the area | Failure of valves (229 off in the ACCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 1.145e-07 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a pipe causes a large inventory of helium to leak into the area | Failure of pipe within the ACCP Hall area (535 metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | 1.605e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a pipe flange causes a large inventory of helium to leak into the area | Failure of pipe flanges (48 off in the TMCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | 4.8e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a safety relief device causes a large inventory of helium to leak into the area. | Failure of safety relief devices (20 off in the TMCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 1e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a valve causes a large inventory of helium to leak into the area | Failure of valves (173 off in the TMCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 8.65e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a pipe causes a large inventory of helium to leak into the area. | Failure of pipe within the TMCP Hall area (1377 metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | 4.131e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | HPGS Room | A person is in HPGS Room "supervised" area and a full rupture of a pipe flange causes a large inventory of helium to leak into the area | Failure of pipe flanges (2 off in the HPGS Room) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | 2e-09 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 + 1 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards) | 8760
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | HPGS Room | A person is in HPGS Rooml "supervised" area and a full rupture of a safety relief device causes a large inventory of helium to leak into the area | Failure of safety relief devices (20 off in the HPGS Room) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 1e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 + 1 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | HPGS Room | A person is in HPGS Room "supervised" area and a full rupture of a valve causes a large inventory of helium to leak into the area | Failure of valves (19 off in the HPGS Room) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 9.5e-09 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 + 1 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | HGPS Room | A person is in HPGS Rooml "supervised" area and a full rupture of a pipe causes a large inventory of helium to leak into the area | Failure of pipe within the HPGS Room area (30 metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | 9e-10 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 + 1 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Dogshed | A person is in Dogshed and a full rupture of a pipe flange causes a large inventory of helium to leak into the area | Failure of pipe flanges (? off in the Dogshed) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | ? | ? | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 | Exit from hazards within the area | ? | 8760
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Dogshed | A person is in Dogshedand a full rupture of a safety relief device causes a large inventory of helium to leak into the area | Failure of safety relief devices (? off in the Dogshed) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | ? | ? | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 | Exit from hazards within the area | ?
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Dogshed | A person is in Dogshed and a full rupture of a valve causes a large inventory of helium to leak into the area | Failure of valves (? off in the Dogshed) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | ? | ? | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 | Exit from hazards within the area | ?
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Dogshed | A person is in Dogshedand a full rupture of a pipe causes a large inventory of helium to leak into the area | Failure of pipe within the Dogshed (? metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | ? | ? | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 | Exit from hazards within the area | ?
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | ACCP Hall | A person enters into ACCP Hall with a large inventory of helium in the Hall | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | 1.58e-07 |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | TMCP Hall | A person enters into TMCP Hall with a large inventory of helium in the Hall | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | 1.86e-07 |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | HPGS Room | A person enters into HPGS Room with a large inventory of helium in the Hall | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | 2.24e-08 |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 + 1 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Dogshed | A person enters into Dogshed with a large inventory of helium in the Room | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | 0 |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 | Exit from hazards within the area | ?
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a pipe flange causes a large inventory of helium to leaks into the area. | Failure of pipe flanges (53 off in the Cold Box hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | 5.3e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a safety relief device causes a large inventory of helium to leak into the area | Failure of safety relief devices (98 off in the Cold Box hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 4.9e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a valve causes a large inventory of helium to leaks into the area. | Failure of valves (479 off in the Cold Box hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 2.395e-07 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a pipe causes a large inventory of helium to leak into the area | Failure of pipe within the Cold Box area (2141 metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | 6.423e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | Dogshed | A person enters into Cold Box Hall with a large inventory of helium in the Hall | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | 4.06e-07 |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 1 | Exit from hazards within the area | ?
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | CTL Gallery | A person is in Cold Box Hall "supervised" area and a full rupture of a pipe causes a large inventory of helium to leak into the area | Failure of pipe within the CTL Gallery (3553 metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. |  | 3e-11 | 1.0659e-07 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a pipe flange causes a large inventory of Nitrogen to leaks into the area. | Failure of pipe flanges (? off in the ACCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | ? | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a safety relief device causes a large inventory of Nitrogen to leak into the area | Failure of safety relief devices (8 off in the ACCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | ? | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a valvecauses a large inventory of Nitrogen to leaks into the area. | Failure of valves (229 off in the ACCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 1.145e-07 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | ACCP Hall | A person is in ACCP Hall "supervised" area and a full rupture of a pipe causes a large inventory of Nitrogen to leak into the area | Failure of pipe within the ACCP Hall area (535 metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | 1.605e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a pipe flange causes a large inventory of Nitrogen to leak into the area | Failure of pipe flanges (48 off in the TMCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | 4.8e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards) | 8760
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a safety relief device causes a large inventory of Nitrogen to leak into the area. | Failure of safety relief devices (20 off in the TMCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 1e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a valve causes a large inventory of Nitrogen to leak into the area | Failure of valves (173 off in the TMCP hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | 8.65e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | TMCP Hall | A person is in TMCP Hall "supervised" area and a full rupture of a pipe causes a large inventory of Nitrogen to leak into the area. | Failure of pipe within the TMCP Hall area (1377 metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | 4.131e-08 | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | ACCP Hall | A person enters into ACCP Hall with a large inventory of Nitrogen in the Hall | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | ? |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | TMCP Hall | A person enters into TMCP Hall with a large inventory of Nitrogen in the Hall | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | ? |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards) | 8760
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a pipe flange causes a large inventory of Nitrogen to leaks into the area. | Failure of pipe flanges (? off in the Cold Box hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 1e-09 | ? | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a safety relief device causes a large inventory of Nitrogen to leak into the area | Failure of safety relief devices (? off in the Cold Box hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | ? | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a valve causes a large inventory of Nitrogen to leaks into the area. | Failure of valves (? off in the Cold Box hall) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 5e-10 | ? | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | Cold Box Hall | A person is in Cold Box Hall "supervised" area and a full rupture of a pipe causes a large inventory of Nitrogen to leak into the area | Failure of pipe within the Cold Box Hall (? metres total) | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation | 3e-11 | ? | During normal operation 2 persons 15 minutes per day. During mantenance 10 persons 8 hours a day | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 3 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards)
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | Cold Box Hall | A person enters into Cold Box Hall with a large inventory of Nitrogen in the Hall | Failure of any devices | ODH Class 0 | Although Accelerator Division classification analysis shows no requirement for an ODH Detector system one has been requested. | Asphyxiation |  | ? |  | 1. ODH detectors (O2iM Oxigraf) 2. ODH personal monitor - including second person rule (minimum of 2 people entering at a time) | 1. Active PSS ODH monitoring and alarm system with sensors at high level and low level Action: Upon detection of oxigen level less than 19.5% an alarm will be triggered in the main control room and when ODH is less than 18% the local ODH evacuation alarms in G04 will be triggered (lights and sounders). | 2 + 2 | Entry to supervised ODH area Exit from hazards within the area | Access control to ODH supervised areas (ESS access cards) | 8760