## Slide 1: ODH Phase 1 Hazard Analysis, Monitor Placement, Installation Progress.
Stuart Birch
www.europeanspallationsource.se
19th September 2017

## Slide 2: Introduction
Hazard Analysis
ODH monitor positions
Installation Update
Critical path items

## Slide 3: ODH Phase 1.
HPGS
ACCP
TMCP
Dog shed
Cold Box Hall
CTL
G02

## Slide 4: Hazard Analysis
Hazard ID | Hazard | Hazard Description
PSS_ODH Hazard_001 | Oxygen deficiency hazard from Helium | Catastrophic failures of devices (valves, flanges pipe etc.) leading to a large inventory of helium entering areas were personnel will be carrying out checks and maintenance or personnel enter an area which has a larger inventory of Helium in that area
PSS_ODH Hazard_002 | Oxygen deficiency hazard from Nitrogen | Catastrophic failures of devices (valves, flanges pipe etc.) leading to a large inventory of Nitrogen entering areas were personnel will be carrying out checks and maintenance or personnel enter an area which has a large inventory of Nitrogen in that area
Hazards

## Slide 5: Hazard Analysis
Initiating Events
ODH Hazard ID | Hazard | Area | Initiating Event
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | ACCP Hall or TCCP hall, HPGS Room, Cold Box Hall or CTL | A person is in an area and a full rupture of either a pipe flange, Relief device, Valve or Pipe causes a large inventory of helium to leak into the area.
PSS_ODH Hazard_001 | Oxygen Depletion Hazard Helium | ACCP Hall or TCCP hall, HPGS Room, Cold Box Hall or CTL | A person enters into an area with Helium hazard within that area.
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | ACCP Hall or TCCP hall, or Cold Box Hall | A person is in an area and a full rupture of either a pipe flange, Relief device, Valve or Pipe causes a large inventory of nitrogen to leak into the area.
PSS_ODH Hazard_002 | Oxygen Depletion Hazard Nitrogen | ACCP Hall or TCCP hall, or Cold Box Hall | A person enters into an area with Nitrogen hazard within that area.
See ODH hazard register V2

## Slide 6: Hazard Analysis

## Slide 7: Hazard Analysis HPGS ODH ETA

## Slide 8: Hazard Analysis FTA Local Alarm(s)

## Slide 9: Hazard Analysis FTA ODH Detection System (Internal)

## Slide 10
Hazard Analysis FTA ODH Detection System (External)

## Slide 11: Hazard Analysis FTA Personal ODH Monitors

## Slide 12: G04 ODH Detector Positions

## Slide 13: G04 ODH Alarm Sounder and Light Positions

## Slide 14: Cold Box Hall ODH Detector Positions

## Slide 15: Cold box hall ODH Alarm Sounder and Light positions

## Slide 16: CTL Detector, Alarm light and Sounder Positions

## Slide 17: Installation update
G04
All monitors Installed
All Micro pipework installed
All cables Pulled
All Containment Installed
All alarm plates installed
To Do:
Tag Devices
Electrical Racks (Critical Path)
Terminate Racks (Critical Path)
Fibre Installation (Critical Path)
Commissioning (Critical Path
Cold Box Hall
Monitors Installed (4 from 9 some relocation)
Micro pipework installed (4 from 9)
All Alarm plates installed
Cables to be pulled
All Containment Installed
To Do:
Electrical Racks (Critical Path)
Terminate Racks (Critical Path)
Fibre Installation (Critical Path)
Commissioning (Critical Path)
Cold Box Hall And CTL Installation to be
completed by 30th September

## Slide 18: Critical Path items
PLC racks 3 off delivery to Processkontroll October
FAT Expected Week 44.
Installation and commissioning will start Week 45

## Slide 19
Thank You