## Slide 1: Beam diagnostics equipment allocation
Johan Norin
www.europeanspallationsource.se
20 November 2017

## Slide 2: Naming service
Names for diagnostics systems (BCM, BLM, EMU)
Names for beamline elements (ACCT, ICBLM, EMUG)
Names for electronics (MTCA, AIU)
The name structure is:
  Section-subsection:Discipline-Device-ID
  SPK-040LWU:PBI-BPM-001

## Slide 3: Cable database
All ”long” cables need to be in the ESS cable database, with their endpoints defined in the naming service.
”Long cables” are cables that goes between the tunnel, through stubs, to electronics racks located elsewhere.

## Slide 4: Rack locations
Location | Number of beam diagnostics racks
Front end building (FEB) | 10
Klystron gallery | 27 (4 free)
Test stand area | 6
Gallery support area (GSA) | 4
Target access area (TAA) | 5 (2 free)
Sum | 52 (6 free)

## Slide 5: Rack electronics allocation
For most systems, electronics have been allocated to racks in order to minimize the cable lengths. Some systems are more sensative to cable lengths than others (BPM, BCM, BLM).
Some systems should not be mixed in the racks. Noisy and sensitive equipment must be separated.
Cables from the same area in the accelerator are routed together as much as possible.
The number of beam diagnostics racks is limited.

## Slide 6: Rack electronic allocation
Boxes represents crates and have the correct size in rack units.
All beamline elements are mapped to the racks.
Worst size scenario assumed during planning.
Device | # | Location
BCM | 1 | MBL-010
BPM | 4 | MBL-010 – MBL-020
ICBLM | 20 | SPK-100 – MBL-060
LBM | 1 | MBL-010

## Slide 7: Cable endpoint information status
All systems are allocated to racks.
All beamline element locations are defined.
Approximate routing for each beamline element is done.
Cable lengths for all systems can be reviewed!

## Slide 8: Cable lengths – PBM
Chart: BPM
Cables in the front end building is shorter, as the racks are on the same floor as the tunnel.
Typical rack to tunnel distance: 45 m.
Peaks corresponds to stretches with no racks.

## Slide 9: Device grouping – ICBLM
Some systems are not routed the shortest way.
The ICBLM system uses an alternating rack routing for higher redundancy.
Chart: 

## Slide 10: Device grouping – ICBLM
Chart: 
Some systems are not routed the shortest way.
The ICBLM system uses an alternating rack routing for higher redundancy.

## Slide 11: Cable database status
Cable endpoint for all systems are selected.
Cable types for all systems with beamline elements in the warm linac are selected, and entered into the database.
Present cable count: 1687 cables, 84.1 km

## Slide 12: Cable type harmonization
We are presently reviewing and reassigning cable types.
The goal is to minimize the number of cable types in order to facilitate the spare cable allocation.
We have reduced the number of cable types from 24 to 15. The largest reduction is for control cables.
” As simple as possible, but not simpler.”

## Slide 13: Cable harmonization – unique cables
Original cable | Count | Selected cable | Cable type | System | Purpose
2C19OSHFRH | 57 | 2C19OSHFRH | Mulrad-2 | BCM | Signal
3/8"RF coaxial_HF | 516 | 3/8"RF coaxial_HF | Heliax | BPM, BCM | Signal
2YC2YC(St)H | 377 | 2YC2YC(St)H | Triax 70 Ω, Cern | BLM | Signal
2xC(St)H | 212 | 2xC(St)H | Triax 50 Ω, Cern | BLM,NPM | HV
14P20IOSHF | 11 | 14P20IOSHF | 14 TP, AWG20 | WS | Signal
25P24OSHF | 2 | 25P24OSHF | 25 TP, AWG24 | EMU Grid | Signal
Signal cables!
Three types of optical fibres (not included in table)
Standard AC power

## Slide 14: Cable harmonization – standarized cables
Original cable | Count | Selected cable | Cable type | System | Purpose
1C20RG-58HV | 13 | 1C20RG-58HV | RG-58 HV | &FC,EMU | Signal, HV
1C13RG-213HF | 1 |  |  | EMU | HV
1C13RG-214HF | 1 |  |  | FC | HV
3C21OSHF | 17 | 3C21OSHF | 3 conductors | nBLM, EMU | LV, Control
3C0,34OSHF | 24 |  |  | WS, EMU | Motion
6C20OSHF | 160 | 5P20IOSHF | 2 x 5 TP, AWG20 | NPM | Motion, Signal
4PR18OTC3V | 39 |  |  | MEBT actuators | Motion
4P21IOSLSHF | 52 |  |  | EMU, WS, COLL | Motion
5P20IOSHF | 14 |  |  | WS | Motion, Signal
10C20OSHF | 19 |  |  | NPM, DPL | Motion
6P19OSHF | 15 |  |  | WS | Motion
 | 18 | 6P20IOSHF | 2 x 6 TP AWG20 | NPM | Control
6P20IOSHF | 9 |  |  | WS, FC | Motion
12C18NSHF | 1 | 12C18IOSHF | 12 conductors, AWG18 | MEBT FC | HV, control
12C18IOSHF | 1 |  |  | MEBT EMU | HV, control

## Slide 15: Spare cable strategy
We plan to add an additional 10-20% of cables.
Spare cables will in general be routed from a rack to the stub exit in the tunnel.
Specialized cables will be routed to actual endpoint positions (e.g. BCM mulrad cable).
Spare planning is ongoing.

## Slide 16
Thank you!

## Slide 17: Extra - ICBLM cable lengths
Chart: 

## Slide 18: Extra – nBLM cable lengths
Chart: nBLM

## Slide 19: Extra – BCM cable lengths
Chart: BCM
| LEBT-010:PBI-BCM-001 | RFQ-010:PBI-BCM-001 | MEBT-010:PBI-BCM-001 | MEBT-010:PBI-BCM-002 | DTL-010:PBI-BCM-001 | DTL-020:PBI-BCM-001 | DTL-030:PBI-BCM-001 | DTL-040:PBI-BCM-001 | DTL-050:PBI-BCM-001 | MBL-010LWU:PBI-BCM-001 | HBL-010LWU:PBI-BCM-001 | HEBT-010LWU:PBI-BCM-001 | HEBT-160LWU:PBI-BCM-001 | A2T-010LWU:PBI-BCM-001 | A2T-090DRF:PBI-BCM-001 | A2T-130DRF:PBI-BCM-001 | DMPL-010DRF:PBI-BCM-001 | DMPL-040DRF:PBI-BCM-001
BCM | 23 | 28 | 26 | 26 | 34 | 41 | 38.5515 | 39.2957 | 39.4723 | 30.3248 | 38.4526 | 30.3248 | 55.4926 | 66.0051 | 51.1408 | 56.492 | 64.8642 | 82.4913

## Slide 20: Extra – BPM distribution with RL taps

## Slide 21: Extra – nBLM