## Slide 1
Carlos A. Martins
ESS – Accelerator Division - RF Electrical Power Systems
www.europeanspallationsource.se
Critical Design Review on 660kVA klystron modulators for RFQ/DTL and MBeta
S5.1 – Calculations, Simulations and Preliminary Test Results

## Slide 2
LV power conversion stage design
- Simplified electrical schematics

## Slide 3
LV power conversion stage design
- AC line filter (by Jema)
Selected components
· Reactor:
  - L= 30uH, Irms(50Hz) = 750A, Ipk = 1100Apk;
  - 3 phases;
  - Manufacturer: Eremu ref. 65-750m030;
  - Number of components: 1 unit;
· Capacitors:
- C= 400uF, 350Vrms, 70Arms
- Manufacturer: Electronicon 200μF ref. E62.P17-204C60
- Number of components: 2 units in parallel per phase.
· Resistors:
- R= 50mΩ, 250W, low inductance.
- Manufacturer: Ohmite 100mΩ ref. TGHLVR100JE
- Number of components: 2 unit in parallel per phase and in series with the capacitor.
For further details, see:
“ESS-Lund - Klystron Modulators, AC Line Filter”, Report issued by Jema on 04/12/2017
Gain (IR / ICV), dB
IR, IS, IT in nominal operation, steady state

## Slide 4
IR, IS, IT
MCB
Pre-charge
50A
200ms
MCB
Pre-charge
IR, IS, IT
0.5kA
50ms
LV power conversion stage design
- AC line filter (by Jema)
Start-up with Pre-charge
Pre-charge
MCB
IR, IS, IT
0.5kA
5s

## Slide 5
LV power conversion stage design
- Power stacks (by Semikron)
H-bridge (DC/AC) (x6)

## Slide 6
LV power conversion stage design
- Power stacks (by Semikron)
For further details, see:
“Technical Report for project ESS Full Scale Klystron Modulator”, rev. 4, Report issued by Semikron on 20/01/2017
AC/DC
DC/DC
Thermal calculations
modules disposal on heatsink
AC/DC
DC/DC
RthH = 0.06 °C/W per module @ 10 l/min water flow

## Slide 7
LV power conversion stage design
- Power stacks (by Semikron)
For further details, see:
“Technical Report for project ESS Full Scale Klystron Modulator”, rev. 4, Report issued by Semikron on 20/01/2017
Fsw = 15kHz
Uin = 1000V
Uout = 1000V max.
Iout = 2600Apk
Tpulse = 3.5ms
PRR = 14Hz
TW = 27 °C
Thermal calculations
H-bridge

## Slide 8
LV power conversion stage design
- AC line and DC inductors (by MagComp)
For further details, see:
“Datasheet MagChoke 3*600 uH, 245Arms”, rev. 4, issued by MagComp on 24/10/2017
AC line, 3-phase inductor
Axis symmetric cut view of the 3 cores (full 3-phase inductor)
Thermal plot
Note: Temperatures are in Kelvin
(386 K = 115 °C)

## Slide 9
LV power conversion stage design
- AC line and DC inductors (by MagComp)
For further details, see:
“Datasheet MagChoke 4mH, 240Arms”, rev. 2a, Report issued by MagComp on 25/10/2017
DC inductor
Note: Temperatures are in Kelvin
(405 K = 135 °C)
Axis symmetric cut view of the cores (full DC inductor)
Thermal plot
Note: Temperatures are in Kelvin
(371 K = 100 °C)

## Slide 10
LV power conversion stage design
- DC link capacitors’ discharge systems
Discharge time below 50V: 0.8s
Discharge peak power: 2 x 6.3 kW
Rugged type: each resistor accepts 5x nominal power for 10sec
Resistors:
  - RDS A1, A2 (DC-link bus A);
  - RDS B1, B2 (DC-link bus B);
  - RDS C1, C2 (DC-link bus C);
For a each DC-link bus:
2 x (47 Ω / 1000V / 800W) in series
Contactors:
  - KDS A1, A2 (DC-link bus A);
  - KDS B1, B2 (DC-link bus B);
  - KDS C1, C2 (DC-link bus C);
For a each DC-link bus:
LTC 100 type, 1-pole, NC
Rugged type, railway applications

## Slide 11
LV power conversion stage design
- Main capacitor bank discharge systems)
For a each main capacitor bank:
2 x (2 Ω / 1000V / 10 shots 50kJ) in series;
Discharge time below 50V: 1.2s
Discharge peak power: 2 x 125 kW
Manual grounding switch
Discharge contactor

## Slide 12
HV oil tank assembly stage design
- HVHF transformer
Electromagnetic calculation of the HVHF transformers:
Results of magnetostatic FEA computation
HVHF transformer
HV Rectifier Box
Measured in low signal (LCR meter)
@D. Anderson’s report: Lm=1.649 mH,
at 50 Hz
Short circuit, magnetic flux
Open circuit, magnetic flux
Magnetizing inductance,
computed by FEM
HV module
Leakage inductance,
computed by FEM
Measured in low signal (LCR meter)
@D. Anderson’s report: Lσ=437.5 µH,
at 50 Hz
µ

## Slide 13
Rectifier PCB unit
top side
Bottom side
HV oil tank assembly stage design
- HV rectifier bridge
HV rectifier bridge
Losses on each diode, avg: 2.2W;
Losses on each snubber resistor, avg: <2W;

## Slide 14
HV oil tank assembly stage design
- HV rectifier bridge
HV rectifier bridge
Electric field (V/m)

## Slide 15
HV oil tank assembly stage design
- HV rectifier filter
HV rectifier filter formed by:
Differential mode HV inductor, Lf;
Damped capacitor branch, Cf1+Rf;
Undamped capacitor branch, Cf2+Rd;
Lf = 8mH;
Rf = 2700 Ω / 23 = 117 Ω;
Cf1 = 20 x 1.7nF = 34 nF;
Cf2 = 8 x 1.7nF = 13.6nF;
Rd = 10 Ω;
Lf
Rf
Cf1
Cf2
Rd
Bode plots of the HV rectifier filter
f (Hz)
Gain (dB)
4 klystrons
3 klystrons
f (Hz)
Gain (dB)
2 klystrons
f (Hz)
Gain (dB)
No load
f (Hz)
Gain (dB)

## Slide 16
HV oil tank assembly stage design
- HV inductor

## Slide 17
HV oil tank assembly stage design
- HV inductor
Note: This inductor was an earlier prototype designed for LDM = 16mH (old design)

## Slide 18
HV oil tank assembly stage design
- HV capacitors & damping resistors

## Slide 19
HV oil tank assembly stage design
- HV module electrostatic design
Electromagnetic calculation of the HVHF transformers:
Results of electrostatic FEA computation
Electric field over horizontal plane (@ top anti-corona level)
Stray capacitances modelling
@115 kV

## Slide 20
Simulation Results (Reduced Scale Prototype)
Part I – LV capacitor charger module
(AFE + DC/DC with capacitor bank and pulsed dummy load)

## Slide 21
Simulation Results (Reduced Scale Prototype)
Part I – LV capacitor charger module
(AFE + DC/DC with capacitor bank and pulsed dummy load)

## Slide 22
Simulation Results (Reduced Scale Prototype)
Part I – LV capacitor charger module
(AFE + DC/DC with capacitor bank and pulsed dummy load)

## Slide 23
Simulation Results (Reduced Scale Prototype)
Part II – HV amplification
(H-bridges + Stacked HV modules)
PI

## Slide 24
Simulation Results
Part II – HV amplification
(H-bridges + Stacked HV modules)

## Slide 25
Simulation Results
Arc Protection
Klystron voltage (V)
Arc Energy (J)
time (s)
Klystron Current (A)
< 6J

## Slide 26
Experimental Results
Part I – LV capacitor charger module
(AFE + DC/DC with capacitor bank and pulsed dummy load)

## Slide 27
Experimental Results
Part II – HV amplification
(H-bridges + Stacked HV modules)

## Slide 28
Prototyping and testing of main sub-systems
ESS has decided to purchase and test some key sub-systems
(In parallel with the call for tenders for the series production)
DC/AC H-bridge, from Semikron;
Production and assembling of a complete HV module
+
-

## Slide 29
Test Setup
Cap. charger + H-bridge + HV module prototype
Cap. charger
(1kV / 10kW)
H-bridge
(1kV / 2600Apk)
Main capacitor bank
(1kV / 100mF)
HV module, in oil tank
(1kV / 10kW)

## Slide 30
Test Setup
Cap. charger + H-bridge + HV module prototype
CH1: Cap. bank voltage (200V/div);
CH2: H-bridge output voltage (1kV/div);
CH3: H-bridge output current (1kA/div);
CH4: HV module output voltage (5kV/div);
Zoom over flat-top
Parameters:
1kV charge on cap. bank;
Nominal pulse voltage: 20kV;
Nominal pulse current: 100A;
Nominal pulse width: 3.5ms;
Low pulse rep. rate: 1.4Hz (instead of 14Hz)