## Slide 1
Göran Göransson
ESS – Accelerator Division – RF Group – Power Converters section
www.europeanspallationsource.se
Critical Design Review on 660kVA klystron modulators for RFQ/DTL and MBeta
S5.3 – Reliability Analysis

## Slide 2
Reliability
“Reliability is the probability that a device or a system will function as expected
without failure for a given duration in an environment.”
“Bathtub” curve

## Slide 3: Definitions
During Useful Life, you apply the concepts of reliability, availability, serviceability, and manageability (RASM) engineering. The failure rate “λ” or mean time between failure (MTBF) is considered to be constant, that is:
1/λ = MTBF
MTBF = Mean Time Between Failure
λ = Failure rate
The Failures In Time (FIT) rate of a device is the number of failures that can be expected in one billion (109) device-hours of operation. It is often denoted by the Greek letter λ (lambda)

## Slide 4: The SML Modulator

## Slide 5: Total MTBF for the complete modulator
  Complete SML Modulator
  AC/DC + DC/DC Power stack
H-bridge (DC/AC) Power Stack
  Control System
Internal Power Supplies
  Circuit Breakers and contactors
  HV tank

## Slide 6: AC/DC + DC/DC Power Stack
  One AC/DC + DC/DC Power stack consists of the following:
6 pieces of dual IGBT modules 1700V/400A SKM400GB17E4 used in the AC/DC part: 2.9E8 hours per modules
2 pieces of dual IGBT modules 1700V/400A SKM400GB17E4 used in the DC/DC part: 1.1E8 hours per modules
4 pieces of drivers 1700V/6W 2 channels with adaption board, Skyper 42 LJ: 7.5 E6 hours per module.
3 pieces of LEM current sensors, LF310-S: 2991763 hours per sensor.
1 piece of LEM current sensor, LF510-S: 4974392 hours per sensor.
1 piece of Crow Bar current sensor, HAS 200-S: 6627847 hours per sensor.
7 pieces of Electronicon capacitors 420uF/1100V: 3 FIT per capacitor.

## Slide 7: AC/DC + DC/DC Power stack continued
The other components are of much higher reliability and are therefore not mentioned.
For one AC/DC + DC/DC Power stack this means:
-> MTBF = 513377 hours. This means that for all three modules that we have in one modulator the total MTBF is 171126 hours.

## Slide 8: H-bridge (DC/AC) Power stack
One H-bridge consists of the following:
8 pieces of IGBT modules 1700V/1800A CM1800HC-34N: MTBF 19241870 hours per module
2 pieces of drivers 1700V 2 channel with adaption board, Skyper 42 LJ: 7.5 E6 hours per module.
2 pieces of LEM current sensors, Lilco 58M0020 equivalent to Pearson 4418: 10E6 hours per sensor.
15 pieces of Electronicon capacitors 420uF/1100V: FIT 2 per capacitor.
3 pieces of FFLC46*MC1698: MTBF 268467907 hours per capacitor

## Slide 9: H-bridge (DC/AC) Power stack continued
For one H-bridge Power stack this means:
-> MTBF = 1082718 hours. This means that for the complete H-bridge
(6 H-bridges) in the modulator the MTBF is 180453 hours.

## Slide 10: Control System
The proposed control system comes from National Instruments and is called Compact Rio. The system consists of the following:
1 piece of chassis NI CRIO 9039, MTBF 263735 hours
2 pieces of expansion chassis NI CRIO 9149, MTBF 704166 hour
3 pieces of Module NI9220, MTBF 1522250 hours
8 pieces of Module NI9401, MTBF 1244763 hours
3 pieces of Module NI9482, MTBF 460321 hours
2 piece of Module NI9425, MTBF 1256699 hours
3 piece of Module NI9223, MTBF > 341274 hours

## Slide 11: Control System continued
This means for the whole control system:
MTBF = 31320 Hours

## Slide 12: Internal Power Supplies
Inside the modulator there are a number of power supplies supplying PCB and contactors.
1 piece of 24V/40A power supply PULS QT40.241, MTBF 375000 hours
3 pieces of DC/DC +24V to +15V / 14 A, TRACO TEP 150-2413WI, MTBF 495000 hours
1 piece of 24V/10A power supply PULS CT10.241, MTBF 975000 hours
MTBF= 102534 hours

## Slide 13: Circuit Breakers and Contactors
These components are hard to evaluate because they have normally a specification that indicates the number of cycles it can be used before it fails. A normal cycle at ESS should be 2 weeks with scheduled maintenance. This would in that case give 2 cycles for two week if no trips occur. In this case you have 52 cycles per year. By this reasoning and the fact that one-year is 8760 hours this gives:
1 piece of Main Circuit Breaker remote controllable; MTBF: 33866160 hours
1 piece of Circuit Breaker AUX-1 3P, 400VAC, 16A, 50kA, Electrical and mechanical endurance 10000 cycles, This gives MTBF 1684615 hours
1 piece of Circuit Breaker AUX-4, 3P 690VAC, 90A, 80kA, Electrical endurance 7500 cycles, this gives MTBF 1263462 hours.
1 piece of Circuit Breaker AUX-1 3P, 400VAC, 10A, 50kA, Electrical and mechanical endurance 10000 cycles, this gives MTBF 1684615 hours.

## Slide 14: Circuit Breakers and contactors continued
3 pieces of Contactor KAC A, B and C, Schneider Electric, LC1F330BD, Mechanical durability 10 million cycles, this gives MTBF 1684615385 hours
1 piece of Contactor for pre-charge, Schneider Electric, LC1D25BD, Mechanical durability 1.4 million cycles, this gives MTBF 235846154 hours
6 pieces of 400V-16A Relay with 24V DC excite, contact ratings 100000 cycles, this gives MTBF 16846154 hours
3 pieces of AC Circuit Breaker for pre-charge circuits A, B, C 690VAC/1.6A, with aux. contact. Mechanical switching 100000 cycles, this gives MTBF 16846154 hours
3 pieces of Contactor for pre-charge circuits A, B, C 690VAC/9A, 600000 cycles, this gives a MTBF of 101076923 hours
3 pieces of DC Circuit Breaker for pre-charge circuits A, B, C 800VDC/8A, with aux contact, mechanical durability 20000 cycles, this gives MTBF of 3369231 hours

## Slide 15: Circuit breakers and contactors continued
1/MTBF = 1/33866160 + 1/1684615 + 1/1263462 + 1/1684615 + 3/1684615385 + 1/235846154 + 6/16846154 + 3/16846154 + 3/101076923 + 3/3369231
MTBF =288303 hours

## Slide 16: HV tank
Inside the HV tank there is a lot of components, but they are hard to calculate the lifetime on because most of them are specially made. An important thing about the components in the HV tank is that they are only used for 5% of the time and that means that the reliability gets 20 times higher. One part that the MTBF could be calculated for is the High Voltage rectifier. This consists of the following:
4 pieces of High Voltage Capacitors 33nF/2000V Kemet R76UN23304040J. The lifetime for this capacitor according to Kemets FIT calculation program is 1E9 hours. In total for the whole modulator we have 4*21*2*6 = 1008 capacitors. This gives an MTBF of 992063 hours. This should then be multiplied by 20 so 19841260 hours.
12 pieces of diodes 1200V/30A IDB30E120 from Infineon. The MTBF for this component is according to Infineon 11969892315 hours. In total in the modulator we have 12*21*2*6= 3024 diodes. This gives a MTBF for the modulator of 3958298 hours. This should then be multiplied by 20 so 79165954 hours.

## Slide 17: HV tank continued
8 pieces of resistors 240kohm / 5W smf5240kjt. According to the Military Handbook Reliability prediction the MTBF for a fixed power resistor made in film 27.42E6 hours. For 2016 resistors this gives 13603 hours. This should then be multiplied by 20 so 272059 hours.
12 pieces of resistors 10 ohm, 35 W, 350V TDH35P10R0JE. According to the Military Handbook Reliability prediction the MTBF for a fixed power resistor made in film 30.3E6 hours. For 12*21*2*6 =3024 resistors this gives 10020 hours. This should then be multiplied by 20 so 200397 hours
4 pieces of varistors V480LA40AP 640 VDC. According to “SIOV metal oxide varistors reliability tests” from Epcos the reliability should be above 5E7 hours per varistor. In the total modulator we have 1008 varistors so this means an MTBF of 49603 hours. This should then be multiplied by 20 so 992060 hours.
2 pieces of Wurth connectors with a very high reliability.

## Slide 18: HV tank continued
1/MTBF = 1/19841260 + 1/79165954 + 1/272059 + 1/200397 + 1/992060
MTBF = 102703 hours

## Slide 19: Total reliability
Total reliability
All parts excluding control crates 1/MTBF = 1/171126 + 1/180453 + 1/102534 + 1/288303 + 1/102703
MTBF = 29118 hours
All parts including control crates
1/MTBF = 1/171126 + 1/180453 + 1/31320 + 1/102534 + 1/288303 + 1/102703
MTBF = 15089 hours