## Slide 1
Pedro Gonzalez, ESS Bilbao
Carlos A. Martins, ESS
Critical Design Review on 660kVA klystron modulators for RFQ/DTL and MBeta
S2.2 – Answers to PDR recommendations

## Slide 2
Answers to PDR recommendations
Summary
All recommendations were understood, found very pertinent and carefully analyzed;
Most of them (i.e. ~80%) were entirely endorsed and implemented;
A few of them were endorsed but only partially done until now;
Only 2 (out of 18) were considered but could not be endorsed (see reasons below);

## Slide 3
Answers to PDR recommendations
[JIRA] (ADR-184) Finalize the interface with ICS requirements prior to release of the request for quote.
The interface with ICS requirements needs to be finalized prior to release of the request for quote. This should include: HMI, and interlocks connection to the control system. Also the relevant portion of klystron protection shall be well described for the programmers
Answer: Ongoing
It was decided by AD management, upon proposal by the WP leader, the following:
  the internal controller is an integrant sub-system of the modulator system;
  Amongst other things, it includes HMI, interlocks connection from the sensors to the control system, all protections of the klystron;
  The interface point between the internal modulator controller and ICS is at the Ethernet port level and at the Pulse_start ‘trigger’ port levels;
  The communication protocol, list of variables and commands to be exchanged between the modulator and ICS/IOC has still to be defined. However, this is a matter of software development only and must be made in a compromise between functionality and processing/communication capabilities of both sides’ hardware.
This interface with ICS will be further clarified within the coming months. A demonstrator will be implemented in the reduced scale SML prototype in TS1, before June 2018.

## Slide 4
Answers to PDR recommendations
[JIRA] (ADR-185) Generate a prioritized list of items prior to release of the request for quote.
Prior to release of the request for quote, generate a prioritized list of items where vendor engineering services are requested and those items which are required to be built to the ESS specific design. In addition, identify the areas where the vendor will be responsible for equipment performance and areas where ESS will be responsible.
Answer: Done
The SoW includes the following sections:
  1.2.1 Items included in the supply;
  1.2.2 Items not included in the supply;
  1.3 Items lent by ESS during execution of the contract;
  2.1 ESS responsibilities;
  2.2 Contractor’s responsibilities;
ESS is responsible for the HV oil tank assembly design 100%, for the ;
The contractor is responsible for the selection of some LV components, for the water cooling implementation; for the cabling selection; for the AC line filter; for the PCB design and production (ESS has lent the PCB files used in the reduced scale SML prototype), industrialization , assembly, testing implementation;
All responsibilities’ sharing between ESS and Jema appear now to be clear.

## Slide 5
Answers to PDR recommendations
[JIRA] (ADR-186) Make an additional galvanic connection between the klystron transformer tank and modulator transformer tank.
An additional galvanic connection between the klystron transformer tank and modulator transformer tank shall be made
Answer: Done
One PE cable (green/yellow), cross section 35mm2, will be installed between each modulator transformer tank and each klystron tank. Each one of these cables will follow the respective HV cable and return cable (ensemble with cable ties)

## Slide 6
Answers to PDR recommendations
[JIRA] (ADR-187) Consider an air cushion solution for movement of the modulators in the tunnel gallery
Consider an air cushion solution for movement of the modulators in the tunnel gallery
Answer: Considered but not endorsed
This would require a compressed air distribution system along the corridor of the G02 gallery, over about 500m, with different outlets to pick up the air;
Also the RF cells would need to be equipped with such outlets in order to move the modulators in this area also;
The width of the corridor is quite narrow in some places, giving a clearance of only about 80 cm on each side of the modulator. The displacement in such narrow corridor, over such long distances, would require extreme care and displacement control;
Personnel safety concerns in case the modulator (7 tons, 4 meters long, 1.4meters wide) would slip out of control over the air cushion, potentially hitting some of the transportation operators

## Slide 7
Answers to PDR recommendations
[JIRA] (ADR-188) Review buss bar connections between HV and LV for easier maintainability
Review buss bar connections between HV and LV for easier maintainability
Answer: Considered but not endorsed
It was understood that maintenance would be facilitated by twisting the busbars by 90 degrees;
However, this manoeuvre would be difficult to implement from the mechanical point of view, without significantly changing the layout of the whole modulator;
Also, in the twisting process, it would be difficult to maintain both bars of the busbar close to each other therefore keeping their leakage inductance minimal;
The isolation sheets would also need to be twisted which could lead to some weak insulation points;
It was judged that the assembling/disassembling of the busbars with the present configuration can still be done reasonably well with an adequate set of tools and, if needed, by using a mirror placed behind the connection points to orient the insertion of the keys into the screws/nuts. Will be shown in session 3.2

## Slide 8
Answers to PDR recommendations
[JIRA] (ADR-189) Review the Bill of Materials to ensure it contains all necessary items
Review the Bill of Materials to ensure it contains all necessary items including those to be developed by the vendor prior to request for quote. The BOM as presented had many parts which are ‘tbd’, and also Farnell references (one should consider specifying the component manufacturer and part number).
Answer: Done
The Bill Of Materials (BOM) was updated and very well discussed with Jema in detail. Will be presented in session 3.3;
The BOM is now at about 95% of completion, and the remaining components to be identified are non critical;
Jema will update and control the references, manufacturers, etc. in the list according to their usual procedures;
According to the SoW, the realization of the final BOM list is the responsibility of Jema.

## Slide 9
Answers to PDR recommendations
[JIRA] (ADR-190) Improve the maintainability of the modulator and define specifications for RAMI.
Prior to releasing the request for quote, work with the RAMI expert to improve the maintainability of the modulator and define specifications for RAMI. Use this analysis to identify areas where higher safety margins might be employed to improve the reliability. manufacturer and part number).
Answer: Done
A detailed MTBF calculation was done by Goran Göransson and communicated to the RAMI expert (Enrico Bargalo). Will be presented in session 5.3;
Considerable safety margins were adopted throughout the whole design; increased with respect to the SML reduced scale prototype:
  >20% on the power rating of all inductors;
  >50% on the power rating of all resistors;
  >40% on voltage rating of all capacitors;
  >100’000 hours on lifetime expectations for all components, including power semiconductors operating in pulsed mode (i.e. subject to thermal cycling);
  Extra insulation sheets in the busbars and HV transformer windings;
  Only well proven active components were employed, COTS and well documented by datasheet;

## Slide 10
Answers to PDR recommendations
[JIRA] (ADR-191) Estimate the inductance values and assess the impact on the voltage transients generated during switching events.
The fuses proposed for the H-bridge will likely introduce additional stray inductance. Estimate the inductance values and assess the impact on the voltage transients generated during fast high current switching events to assure IGBT ratings are not exceeded. Include the fuses on any additional bridge prototype(s) deployed and measure VCE during switching events
Answer: Done
The presence of the fuses did not create any relevant voltage transients during switching. This was experimentally evaluated by the waveforms recorded on the testing of the full scale HV module prototype using the final H-bridge power stack from Semikron.
Indeed, after the fuse, the H-bridges have a “local” capacitor bank very close to the IGBT’s, and without fuses in series. This local capacitor bank is of about 6mF @1kV and it avoids voltage transients due to switching of the IGBT’s
Will be presented in session 5.1;

## Slide 11
Answers to PDR recommendations
[JIRA] (ADR-192) Hold a separate electrical safety review concurrent with the CDR.
Hold a separate electrical safety review concurrent with the CDR
Answer: Done
The safety review was held on 13th March 2018, from 13h30 to 17h30.

## Slide 12
Answers to PDR recommendations
[JIRA] (ADR-193) Give priority to the use of ester oil for safety reasons.
Give priority to the use of ester oil for safety reasons. As a backup, work with the ES&H department to find acceptable ways to use other oil solutions if required by modulator performance
Answer: Done
The utilisation of ester oil for safety reasons was tried out to the maximum possible extent;
However, it was found that above 100kV, the electrical insulation is not reliable. Tests were carried out with the full scale HV module (see report from David Anderson) and breakdown was found at about 100kV during Hipot testing. With mineral, similar Hipot tests resulted in successful insulation tests up to 140kVdc/1 min;
SwissFEL initially planned to also use MIDEL 7131 in their modulators, but were forced to change back to Mineral oil after initial testing;
Very detailed documentation was published since 6 years ago, clearly identifying a huge reduction of voltage breakdown strength of MIDEL7131 wrt Mineral oil, particularly with non homogeneous electrode surfaces and negative polarities;
David Anderson, from SNS, also reported several issues with their ester oil.

## Slide 13
Answers to PDR recommendations
[JIRA] (ADR-194) Repeat the test of the reduced scale prototype using ester oil installed under vacuum conditions.
Give priority to the use of ester oil for safety reasons. As a backup, work with the ES&H department to find acceptable ways to use other oil solutions if required by modulator performance
Answer: Ongoing
We consider this would have been good to do;
Not done due to lack of time;
Instead, it was given priority to the utilisation of mineral oil for the modulators to be installed in the machine;
Discussions with ES&H have been initiated;

## Slide 14
Answers to PDR recommendations
[JIRA] (ADR-195) Fabricate a prototype and demonstrate the ability of the module to hipot to conservative values under oil.
30% additional clearance was added to the HV module clearances based on prototype hipotting results. Fabricate a prototype and demonstrate the ability of the module to hipot to conservative values under oil
Answer: Done
A full scale HV module was built according to final drawings;
David Anderson was invited and accepted to lead the testing at LTH, TS1, in order to have an independent assessment;
A test report was written by David Anderson (see annexes);
Two main issues were found and needed correction:
  Hipot testing did not pass the specifications (150kVdc/1 min) due to spark between the HV box corner and the HV transformer primary terminal leads at 145kVdc/0.5min.
    Corrected by shielding the leads;
  Overheating of the oil on the region of the HV rectifier bridge.
    Corrected by adding extra oil forced circulation inside the HV rectifier box
  - See presentation on session 3.2

## Slide 15
Answers to PDR recommendations
[JIRA] (ADR-196) Develop a strategy for repair.
Develop a strategy for repair of equipment, subsystems and components. Utilize the results from the RAMI analysis to estimate the probability of failure and ensure the design layout supports minimizing the mean time to repair.
Answer: Done
The topology is modular. Each module weights less than 250kg;
In case of a failure in one component/sub-system, only this one needs to be exchanged ;
The placement of components on the LV power conversion cabinet was made in order to reduce MTTR and maximize availability:
  The most sensitive components (that fail more often) were placed immediately in front of the doors;
  The passive components (inductors, resistors, capacitors, contactors, etc.) were placed behind, since these fail much less often;
  The HV oil tank can easily be slide out/in for easy access for repair. All the components inside the tank are assembled into a frame that can be lifted from the tank;
  Complete modulator can be easily removed and transported as a single unit. Embedded wheels;
  Spare parts deployed in 3 stages:
    complete modulators ready to go;
    sub-assemblies ready to install: H-bridge power stacks; AC/DC+DC/DC power stacks; HV modules; Control crates;
    individual components: Control modules, PCB’s, resistors, inductors, capacitors, IGBT modules, IGBT drivers, current sensors, voltage sensors, contactors, relays, valves, pumps, flowmeters, HV rectifier bridges, HV inductors, etc. see presentation in Session 4.3

## Slide 16
Answers to PDR recommendations
[JIRA] (ADR-197) Consider increasing the sampling rate for the analog signal acquisition system
Consider increasing the sampling rate for the analog signal acquisition system. 100 kSa/s may alias important information that may compromise troubleshooting. Consider buffering data locally, storing data files locally after fault events and time-stamping fault events to aide in troubleshooting while equipment is in operation.
Answer: Done
The sampling rate of the primary currents on the HVHF transformers and of the HV output signal have been increased from 100kSa/s to 1MSa/s. These are the fastest signals of the entire modulator;
Buffering will be done locally on the modulator controller in a circular buffer;
The local buffers will be frozen in case of an event, but the stored data must be pushed out via the Ethernet port to ICS after the fault since the controller does not have local data files storage and time stamping capacity. This is however found to be sufficient;
A set of variables, status and waveforms will be made available in the internal registers and circular buffers ;
See presentation in session 3.4

## Slide 17
Answers to PDR recommendations
[JIRA] (ADR-198) Examine and make more explicit the selection of hoses and connectors in the water cooling system.
Examine and make more explicit the selection of hoses and connectors in the water cooling system.
Answer: Done
The components of the water cooling circuit have been selected from the most reliable manufacturers (stainless steel manifolds, flowmeters and flow switches from ElettaTM, water hoses and nipples from ParkerTM (compatible);
Only stainless steel or copper materials are in contact with the water;
See presentation in session 3.3

## Slide 18
Answers to PDR recommendations
[JIRA] (ADR-199) Put a high priority in the check of the HV transformer in full scale.
Put a high priority in the check of the HV transformer in full scale. There might be technical problems in building this combination of transformer and HV rectifier and filter.
Answer: Done
One prototype of a complete full scale HV module (including the HV transformer) was made at LTH, TS1 and validated successfully;
The assembling procedure was simplified with respect to the reduced scale prototype and the assembling work was made easier. This was verified in practice during the assembling phase;
No issues were found in the design, construction and testing;

## Slide 19
Answers to PDR recommendations
[JIRA] (ADR-200) Consider additional testing time for R&D and improvement on the prototype. e.g. EMI, internal parasitics etc.
Consider additional testing time for R&D and improvement on the prototype. e.g. EMI, internal parasitics etc.. Even after long period of testing and improving of the XFEL modulator (more than 10.000 hrs) problems were found in the series production.
Answer: Done
The reduced scale modulator prototype was tested for an extra period of 100 hours with a real load (klystron);
Indeed some additional were found during this second test phase, but they were understood and corrected;
The issues found during this second testing phase were had already been corrected before the tests took place in the design of the full scale modulator (extra margins had been added already);
For the full scale modulator, the schedule requested by ESS does not allow time for any extra testing and the testing campaign that was foreseen for the 1st unit at ESS must be reduced. This will increase the risks;

## Slide 20
Answers to PDR recommendations
[JIRA] (ADR-201) Carefully monitor and manage the software development time schedule.
Carefully monitor and manage the software development time schedule.
Answer: Ongoing
The software used for the reduced scale prototype will be re-used for the full scale modulators into a great extent;
The state machine needs to be improved slightly;
The HMI needs to be improved slightly;
The principle of “stand alone booting” has been implemented and tested. Still needs to be finalized;
The remote communication protocol and procedure (interface to ICS) needs to be developed entirely;
Local post mortem analysis needs to be implemented entirely;

## Slide 21
Answers to PDR recommendations
Additional recommendation issued by the PDR review committee.
11) Are there sufficient staff resources and competence assigned to the Work Unit team to allow to progress with work in accordance with activities, durations and milestone dates shown in the ESS ACCSYS Project plan?
The resources are stretched thin and additional staff are required for success.
Answer:
The resources situation has not improved since the PDR;
One valuable element of the power converters section has announced resignation recently;
A replacement has been requested but it will take 6 to 8 months to find a substitute;
There is a risk that the substitute does not have the desirable skills and experience, therefore requiring extra training time;
This is a major risk for the mission of WP17 and may have severe consequences in the project, both in terms of quality and schedule.