## Slide 1
Txema de la Fuente (JEMA), Carlos Martins (ESS)
www.europeanspallationsource.se
Critical Design Review on 660kVA klystron modulators for RFQ/DTL and MBeta
S3.3 – Bill of materials

## Slide 2
Bill of materials
Input unit
INPUT UNIT |  |  |  | 
Item |  | Manufacturer | Model | Features
01U01 | EMC FILTER | FUSS | 3F690-800.260 | 800A, 690Vac
01Q01 | MCB | ABB | T7H800 | 800A, 690Vac
01L01 | Lfg | EREMU | 65-750m030 | 30µH, 750A
01C01…06 | Cfg | ELECTRONICON | E62.P17-204C60 | 400 µF, 350V
01R01…06 | Rfg | OHMITE | TGHLVR100JE | 100mΩ, 250W

## Slide 3
Bill of materials
AC/DC + DC/DC Capacitor charger

## Slide 4
Bill of materials
AC/DC + DC/DC Capacitor charger
AC/DC + DC/DC CAPACITOR CHARGER |  |  |  |  | 
Item |  | Manufacturer | Model | Features | 
02K11,31,51 | KAC | SCHNEIDER | LC1F330 | 330A, 1000Vac | 
02L11,31,51 | Lf | MAGCOMP | 911-2030 | 600µH, 245A | 
02A11,31,51 | Charger stack | SEMIKRON | 08801679AA | 220A, 1100V | 
02U14,34,54 | R CB A,B,C | WELWYN | WDBR5-47RKTW | 47Ω, 5kW | 
02Q12,32,52 | CB PRECH | ABB | MS132-1.6 | 1A, 690Vac | 
02,11,31,51 | CB DC PRECH | ABB | S802PV-S10 | 10A, 800Vdc | 
02K12,32,52 | K PRECH | SCHNEIDER | LC1D25BD | 25A, 690Vac | 
02V11,31,51 | RB PRECH DC | SEMIKRON | SKD53/18 | 53A, 1800V | 
02R17..37..57 | R DC PRECH | VISHAY | RPS0500DH47R0JB | 47Ω, 50W | 
02K13,33,53 | K DS | MICROELETTRICA SCIENTIFICA | MS-LTC1001PNCDC | 100A, 1KV | 
02R15..35..55 | R DS A1…6 | TEE | CJT80047RJ | 47Ω, 800W | 
02L12,32,52 | Ldc | MAGCOMP | 911-2031 | 4mH, 240A | 
02L13,33,53 | Lcm | VACUUMSCHMELZE | T60009-L2380-V276 | -- | 
 | Ccm | VISHAY | MKP1848C61010JP4 | 10µF, 1KV | 
 | Rcm | VISHAY DALE | CPF3100R00FKE14 | 100Ω, 3W | 
02A12,32,52 | DC diodes | SEMIKRON | 08801677AA | 600A, 2200V | 

## Slide 5
Bill of materials
DC/AC Inverters
DC/AC INVERTERS |  |  |  | 
Item |  | Manufacturer | Model | Features
03C11…61 | CBK | AVX | FFLC46MMC1698 | 16900µF, 400A
06V01…06 | V METER | SACI | CC3V | 0-1000V
03F11…61 | FHB | BUSSMANN | 170M7803 | 1000A, 1200Vdc
03A11…61 | H bridge stack | SEMIKRON | 08801678AA | 2600A, 1000V
02K14,34,54 | K DS CBK | MICROELETTRICA SCIENTIFICA | MS-LTC1001PNCDC | 100A, 1kV
02R21..41..61 | R DS 1…6 | HVR | SK2620 | 2Ω, 1kV
02R24…64 | R DS 10…60 | HVR | AL708A | 22Ω, 5650J
02Q13 | GSw | SIEMENS | 3KD4060-0PE20-0 | 315A, 1200Vdc
02R23…63 | R GSw 1…6 | HVR | SK2621 | 0.5Ω, 1kV

## Slide 6
Bill of materials
Control. Aux Power supply
AUXILIARY POWER DISTRIBUTION |  |  |  | 
Item |  | Manufacturer | Model | Features
06Q01 | CB AUX 1 | ABB | S803S-B16 | 16A, 400Vac
06G01 | AUX PS 1 | PULS | QT40.241 | 40A, 24Vdc
06G02 | AUX PS 4 | PULS | CT10.241 | 10A, 24Vdc
06G03,04,05 | AUX PS 2 /31 / 32 | TRACO | TEP 150-2413WI | 10A, 15Vdc
06Q02 | CB AUX 2 | ABB | T4H250 | 100A, 690Vac
06Q03 | CB AUX 3 | ABB | S802S-B10 | 10A, 400Vac
06T01 | TRF 1 | EREMU | 21-402BMWW | 4KVA, 600V/400V

## Slide 7
Bill of materials
Control. Racks.
CENTRAL CONTROL SYSTEM |  |  |  | 
Item |  | Manufacturer | Model | Features
06U11 | -- | NI | cRIO-9039 | DSP, FPGA
06U12,13,38 | -- | NI | NI-9220 | 16 AI
06U14,15,16,22,26,27,28,35 | -- | NI | NI-9401 | 8 DI/DO
06U52 | -- | NI | TPC-2230 | Screen
06U53 | -- | NI | NI Moxa EDS-G205-1GTXSFP-T | Ethernet switch
06U21,31 | -- | NI | NI-9149 | FPGA
06U23,24,25 | -- | NI | NI-9223 | 4 AI Diff
06U32,33,34 | -- | NI | NI-9482 | 4 SPST Relay
06U36U37 | -- | NI | NI-9425 | 32 DI

## Slide 8
Bill of materials
Control. PCB
CONTROL AND SIGNAL CIRCUITS (PCB) |  |  | 
Item |  | Manufacturer | Model
06U47 | -- | PROELEK/FALCON | Vmeas
06U43 | -- | PROELEK/FALCON | Imeas
06U44 | -- | PROELEK/FALCON | Pmeas
06U45 | -- | PROELEK/FALCON | Inv current
06U46 | -- | PROELEK/FALCON | Out I V
02U01….03U02 | -- | PROELEK/FALCON | IGBT splitter
06U41,42 | -- | PROELEK/FALCON | Log Itlk
02U11,31,51 | -- | PROELEK/FALCON | Crowbar
01U02…02U53 | -- | PROELEK/FALCON | PTC support
06U50 | -- | PROELEK/FALCON | Vmeter
04A11-U01…42 | -- | PROELEK/FALCON | HV rectifier
02U15,35,55 | -- | PROELEK/FALCON | Common mode filter
05U06 | -- | PROELEK/FALCON | RC snubber ARC
05U01 | -- | PROELEK/FALCON | IGBT adapter ARC
06U100 | -- | PROELEK/FALCON | External port

## Slide 9
Bill of materials
HV oil tank: HV module
HVHF MODULE |  |  |  | 
Item |  | Manufacturer | Model | Features
HVHF TRANSFORMER |  |  |  | 
04T11…61 | HVHFTRF 1…6 | VACUUMSCHMELZE | T60009-L2530-V275 | Nanocrystaline
 |  | CMC Klebetechnik | CMC 38293 | Isolated Copper foil
 |  | BRONYMEC |  | 
HV COMMON MODE INDUCTOR |  |  |  | 
04L11…61 | Lcm 1…6 | VACUUMSCHMELZE | T60009-L2380-V276 | Nanocrystaline
 |  | BRONYMEC |  | 
HV RECTIFIER |  |  |  | 
 | Diode bridge | Customize PCB |  | 
HV INDUCTOR |  |  |  | 
04L12…62 | HVL 1…6 | BALERMA | Silicon steel 237x392 | Silicon steel
 |  | BRONYMEC |  | 
HV FILTER CAPACITORS |  |  |  | 
04A12…62 | HV C | TDK | UHV-12A | 1.7nF, 50kV
04A12…62 | HV R | OHMITE | MOX-5N-3306J | 330MΩ, 6W
 |  | BRONYMEC |  | 

## Slide 10
Bill of materials
HV oil tank: HV output
HV OUTPUT COMPONENTS |  |  |  | 
Item |  | Manufacturer | Model | Features
HV OUTPUT COMMON MODE INDUCTOR |  |  |  | 
04L01 | LcmOut | VACUUMSCHMELZE | T60009-L2530-V275 | Nanocrystaline
 |  | BRONYMEC |  | 
HV OUTPUT CAPACITOR BANK |  |  |  | 
04A01 | HV C | TDK | UHV-12A | 1.7nF, 50kV
 | HV RC 1 | METALLUX | HVI 969.105 | 600Ω, 105W
 | HV RC 2 | METALLUX | HVI 969.71 | 50Ω, 71W
 | HV RC 3,4 | OHMITE | MOX-5N-131007JE | 100MΩ, 6W

## Slide 11
Bill of materials
HV oil tank: HV output
HV OUTPUT COMPONENTS |  |  |  | 
Item |  | Manufacturer | Model | Features
04T01…04 | LEM I PULSE 1,2,3,4 | CAENELS | PCT0024 + 4xWCT100CXHPAA | 100A, 200kHz
04T06 | HV DIV | NORTHSTAR | VD-115B-ESS-100917 | 120kV, 0.25%
04K01…04 | ROSS 1,2,3,4 | ROSS ENGINEERING | E60-NO-80 | Gravity return

## Slide 12
Bill of materials
HV oil tank: Oil cooling system
OIL COOLING SYSTEM |  |  |  | 
Item |  | Manufacturer | Model | Features
04M01 | OIL PUMP MOTOR | HYDAC | VPBM-3-1.0-V-100/70-2.2/400-50 | 2.2kW
-- | OIL HEAT EXCHANGER | HYDAC | HEX S615-100-00-NI/G1" | 100 plates
-- | OIL FILTER | HYDAC | LPF W/HC 160 GE 25 B 1.2/V-A2-B6 | Wire mesh 25µm
04K01 | OIL FLOW SWITCH | HYDAC | HFS 2155-1W-0035-0110-7-S-1-000 | 35-110 l/min
04B02 | OIL MOISTURE | E+E ELEKTRONIK | EE364-T63BEA/AwT021M | 4-20mA

## Slide 13
Bill of materials
Water cooling system

## Slide 14
Bill of materials
Water cooling system
WATER COOLING SYSTEM |  |  |  |  | 
Item |  | Manufacturer | Model | Features | 
-- | 1 | NIERUF | GK04000003 | BALL VALVE DN15 | 
-- | 2 | NIERUF | NV01000003 | NEEDLE VALVE DN15 | 
-- | 3 | ELETTA | GSS15 | FLOW MONITOR DN15 | 
-- | 4 | ELETTA | SP-G | FLOW SWITCH DN15 | 
-- | 5 | WIKA | A52,063 | TEMPERATURE GAUGE | 
-- | 6 | WIKA | 233,50 | PRESSURE GAGE | 
-- | 7 | NIERUF | GK04000005 | BALL VALVE DN25 | 
-- | 8 | NIERUF | NV01000005 | NEEDLE VALVE DN25 | 
-- | 9 | ELETTA | GSS25 | FLOW MONITOR DN25 | 
-- | 10 | NIERUF | FK06010008 | BALL VALVE DN50 | 
-- | 11 | ELETTA | FSS | FLOW MONITOR DN50 | 

## Slide 15
Bill of materials
Arc protection system
ARC PROTECTION SYSTEM |  |  |  |  | 
Item |  | Manufacturer | Model | Features | 
05V01,02 | ARC V1,2 | INFINEON | FZ250R65KE3 | 250A, 6500V | 
05U04,05 | ARC DRIVER 1,2 | CONCEPT | 1SP0335V2M1-FZ250R65KE3 | 2.5W, 6500V | 
05U02,03 | ARC DC-DC 1,2 | CONCEPT | ISO5125I-65 | 5W, 6500V | 
05R01,02 | ARC R1,2 | HVR | SR0250 | 12Ω, 1.5W | 
05R03,04 | ARC R3,4 | HVR | AB 061 | 40Ω, 9W | 
05C01,02 | ARC C1,2 | WIMA | SNMPU042008L1IKS00 | 2µF, 2000Vdc | 
05R05,06 | ARC V1,2 | LITTLEFUSE | V751BA60 | 970Vdc, 2600J | 
05R07 | ARC V3 | LITTLEFUSE | V131BA60 | 130Vdc, 450J |