## Slide 1
Carlos A. Martins
ESS – Accelerator Division - RF Electrical Power Systems
www.europeanspallationsource.se
Critical Design Review on 660kVA klystron modulators for RFQ/DTL and MBeta
S5 – Interfaces

## Slide 2
Interfaces to Conventional Power (CNPW)
AC mains supply conditions (CNPW)
The klystron modulator will comply with the following mains supply conditions, both on the AC power port and AC control port:
Nominal values, power port: 600 V AC, 50 Hz, 660kVA, 3P + PE, TNS earthing system;
Nominal values, control port: 400 V AC, 50 Hz, 2kVA, 3P + N + PE, TNS earthing system;
Max. operating variations, step changes, permanent: ± 10 %
Max. phase imbalance: ± 1.5 %
Max. total harmonic voltage-distortion: 10% r.m.s.
Max. Frequency variation: ± 0.5%
Short-circuit power: 14 to 35 MVA
Max. Peak mains surges, phase-to-phase: 1.5 kV for 0.2 ms
Max. mains over-voltage: 1.5 x nominal value for 20 ms
Dips in the mains supply of up to 100 ms duration and varying amplitudes, in one or more of the 3 phases, may occur.

## Slide 3
Interfaces to Conventional Power (CNPW)
AC grid power quality
The SML klystron modulators have been designed in a way that maximizes the power quality at the AC grid (AC power port).
The power quality definition comprises the following three terms: 1)- the voltage flicker; 2)- the low frequency current harmonic emissions; 3)- the power factor.
With an AC power grid having a short circuit power of Scc=14MVA (worst case condition):
Flicker levels
  The maximum voltage amplitude variation at the modulators’ AC terminals, measured at each half cycle, shall not exceed ±0.3% of the nominal voltage;
Low frequency line current harmonics
  The emission of low frequency current harmonics into the AC power port shall comply with the following limits (relative to the fundamental):
  H5 (250Hz): 3%;
  H7 (350Hz): 2.5%;
  H11 (550Hz): 2.5%;
  H13 (650Hz): 2%;
The THD (Total Harmonic Distortion) on the current line shall not exceed 5%.
Power factor
  The power factor, computed over a pulse repetition cycle, will be greater than 0.98.

## Slide 4
Interfaces to Conventional Power (CNPW)
Physical connections
AC cables, power port
AC cables, control port

## Slide 5
Interfaces to RF systems (RF SYS)
Compliance with functional parameters specified in the table of Session 2.1: modulator requirements
Four high voltage cables and sockets shall be used for the high potential outputs (HV1-, HV2-, HV3-, HV4-). The reference shall be:
  - 160KV Receptacle ALI FLANGE Type S51041, equipped with FLANGE 160KV (R24) SPRUNG Type T22179 from ESSEXTM (United Kingdom);
  - 160KV EURO SOLID TIP, ZERO SMOKE JACKET - CABLE TYPE C2042 Type A59037/04M
  from ESSEXTM (United Kingdom);
Four LV return cables, black copper 35mm2, will be used for the low potential output (HV1+, HV2+, HV3+, HV4+);
Four grounding cables, yellow/green copper 35mm2, will be used as an extra grounding link between the modulators and each klystron;

## Slide 6
Interfaces to RF systems (RF SYS)
Physical connections
Picture of one HV socket
Klystrons
Klystron grounding cables (Gnd1, Gnd2, Gnd3, Gnd4)
LV return cables
(HV1+, HV2+, HV3+, HV4+)
Modulator oil tank
HV output sockets
(HV1-, HV2-, HV3-, HV4-)

## Slide 7
Interfaces to Water Cooling (WTCO)
Inlet and outlet manifold plugs
  Size: DN40
  Inlet/outlet couplings’ type: TC (t.b.c.)
The klystron modulators shall comply with the following water cooling circuit conditions:
  Type of water: Demineralized
  Maximal water conductivity: 1.2 µS/cm
  Operating inlet pressure (90% of working time): < 10 bar
  Maximum inlet working pressure: 13 bar
  Maximum inlet temperature: 27ºC
  Maximum inlet/outlet temperature rise: 10ºC
  Maximum inlet/outlet pressure drop: 3 bar
  Minimum flow: 100 liters/min.

## Slide 8
Interfaces to Water Cooling (WTCO)
Physical connections
To be designed by Jema

## Slide 9
Interfaces to RF Local Protection System (RF LPS)
Remote hard control port (RF LPS)
Direct wired connection between the klystron modulator controller and the external RF Local Protection System;
The following logic and analogue signals shall be exchanged through this port:
  POWERING_FAILURE: Sum of klystron modulator internal faults. Indicates that the klystron modulator has at least one internal fault and is therefore at “off” state;
  PC_CONNECT: External cable connected. Indicates that the external cable, linking the klystron modulator to the RF Local Protection System is connected at both ends;
  PC_FAST_ABORT: External fast interlock from the RF general controller. Indicates an external order for a fast stop of the klystron modulator. Shall be treated identically to the internal fast stop red button or door open interlocks;
  HV_PERMIT: HV Pulse Permit. Enables/Disables the klystron modulator to pulse. If deactivated, the klystron modulator shall inhibit the HV pulse by inhibiting all H-bridge IGBT’s, however all capacitor banks shall remain charged and all auxiliary systems shall remain “on” and ready for subsequent pulsing when this signal is enabled again. During its deactivation period, the modulator will keep its same operating state;
  K1,2,3,4_ENABLE: Klystron Enable. Directly controls the state of the Ross HV relays;
  Uk: Analogue signal for read-back of output pulse voltage waveform;
  Ik1,2,3,4: Analogue signals for read-back of output pulse current waveforms.

## Slide 10
Interfaces to RF Local Protection System (RF LPS)
Physical connections
Remote hard control port (RF LPS)
A shielded cable with at least 14 twisted pairs, provided by ESS WP8, will be used for interfacing the klystron modulator with the RF-LPS system;
The connector on the klystron modulator side shall be a metallic 28 pole female Burndy/Souriau® UTO series for wall mounting, with the following pin assignment:
The connector will be placed in the controls enclosure
Name of signal | Direction (with respect to the klystron modulator) | Pin number on connector | Cable Wire # | Logic level or analogue level
POWERING_FAILURE+ | output | Pin 1 | 1 | Failure: Transistor open
POWERING_FAILURE- |  | Pin 2 | 2 | 
Ik4+ | output | Pin 3 | 3 | Low output impedance analogue signal: 0..10V (10V=25A)
Ik4- |  | Pin 4 | 4 | 
PC_CONNECT+ | output | Pin 5 | 5 | Connected: Pins 5 & 6 short circuited
PC_CONNECT- |  | Pin 6 | 6 | 
PC_FAST _ABORT+ | input | Pin 7 | 7 | Not Fast Abort: Pins 7 & 8 short circuited
PC_FAST _ABORT- |  | Pin 8 | 8 | 
Uk+ | output | Pin 9 | 9 | Low output impedance analogue signal: 0..10V (10V=110kV)
Uk- |  | Pin 10 | 10 | 
Ik1+ | output | Pin 11 | 11 | Low output impedance analogue signal: 0..10V (10V=25A)
Ik1- |  | Pin 12 | 12 | 
Ik2+ | output | Pin 13 | 13 | Low output impedance analogue signal: 0..10V (10V=25A)
Ik2- |  | Pin 14 | 14 | 
Ik3+ | output | Pin 15 | 15 | Low output impedance analogue signal: 0..10V (10V=25A)
Ik3- |  | Pin 16 | 16 | 
Spare |  | Pin 17 | Pin 17 | -
 |  | Pin 18 | Pin 18 | -
HV_PERMIT+ | input | Pin 19 | Pin 19 | HV Pulse Permit (H-bridge IGBT’s enabled): Pins 19 & 20 short circuited
HV_PERMIT- |  | Pin 20 | Pin 20 | 
K1_ENABLE+ | input | Pin 21 | Pin 21 | K1 HV relay closed: Pins 21 and 22 short circuited
K1_ENABLE- |  | Pin 22 | Pin 22 | 
K2_ENABLE+ | input | Pin 23 | Pin 23 | K2 HV relay closed: Pins 23 and 24 short circuited
K2_ENABLE- |  | Pin 24 | Pin 24 | 
K3_ENABLE+ | input | Pin 25 | Pin 25 | K3 HV relay closed: Pins 25 and 26 short circuited
K3_ENABLE- |  | Pin 26 | Pin 26 | 
K4_ENABLE+ | input | Pin 27 | Pin 27 | K4 HV relay closed: Pins 27 and 28 short circuited
K4_ENABLE- |  | Pin 28 | Pin 28 | 
similar connector
exact connector (female)

## Slide 11
Interfaces to Integrated Control System (ICS)

## Slide 12
Interfaces to Integrated Control System (ICS)
Remote fieldbus port (ICS)
The remote fieldbus port will be TCP/IP over Ethernet with RJ45 connector;
The same functionalities will be present both on this port and on the local digital port (also Ethernet);
The exact command list will be defined by ESS (WP17 and ICS) in agreement with the Contractor.

## Slide 13
Interfaces to Integrated Control System (ICS)
External pulse trigger port (ICS)
An independent connector compatible with a twisted pair shielded cable will be used for each one of these three signals. The connectors in the klystron modulator will be Lemo® 0B Series, 2 pole female panel mount, ref. EGG.0B.302.CLL
Name of signal | Direction (with respect to the klystron modulator) | Pin number on connector | Cable Wire # | Logic level
Connector 1 (PLS_START) |  |  |  | 
PLS_START+ | input | Pin 1 | 1 | Pulse Start: Pins 1 & 2 short circuited
PLS_START- |  | Pin 2 | 2 | 
Pin assignment for the “external pulse trigger port” connectors
        Monitoring of status, interlocks, signals and parameters (ICS)
The klystron modulator status, interlocks and control parameters will be available online through both the local digital port and remote fieldbus port. Furthermore, this data will be also consultable from the HMI display at any time, including during “on” stage.
Monitoring of operating stages;
Monitoring of local/remote control modes;
Monitoring of pulse characteristics;
Indication of first fault and list of faults; Monitoring of faults and warnings; Reset;

## Slide 14
Interfaces to Personnel Protection System (PSS)
PSS Shutdown mode (PSS)
As requested by PSS, the “Under-Voltage Release coil” of the MCB (UVR coil in case of ABB) will have 2 dry switches in series with it;
The switches can be exclusively controlled remotely by the PSS system;
The purpose being to ensure that the modulators are at “off” state and de-energized in case of an access into the tunnel;
These dry switches will be placed in the PSS box, mounted on the modulator panel, external side, located in the vicinity of the MCB;
The control cable between the PSS box and the “UVR Coil” of the MCB, internal to the modulators, will be placed in a rugged conduit, with the same color of the PSS box in order to avoid accidental disruptions or disconnections during maintenance.
PSS box

## Slide 15
Interfaces to RF Gallery
The equipment will be installed in the RF Gallery in the RFQ and DTL sections and on the Medium Beta section;
It will be operated remotely and continuously i.e. 24 hours per day, ~250 days of the year;
Maintenance is restricted to shutdown periods and is foreseen to take place only once per year.
Environmental conditions
The klystron modulators shall comply with the following environmental conditions:
Altitude above sea-level: 0 m to 400 m
Ambient temperature variation (operation): +10 °C to +30 °C
Ambient temperature variation (storage): -10 °C to +40 °C
Relative humidity (operation): 10% to 75%
Relative humidity (storage): 30% to 90%
Dimensions
The external dimensions of the complete klystron modulator comply with the following values:
Max. Width: 3.8 meters;
Max. Depth: 1.4 meters;
Max. Height: 2.4 meters.
Heat load into air at G02:
Power losses in air: < 5kW per modulator

## Slide 16
Position of the interface points in the G02 gallery and in the modulator
Conventional power (CNPW):
1- AC power cables, power port;
2- AC power cable, control port (from UPS or LV feeder);
(both cables are within WP15 scope)
AC power input terminal box
AC power input terminal box

## Slide 17
Position of the interface points in the G02 gallery and in the modulator
RF amplifiers (RF-SYS):
1- HV output cables (4x);
2- LV return cables (4x);
3- Grounding cables (4x);
(All cables are within WP17 scope)
HV output sockets (4x)
HV output sockets (4x)

## Slide 18
Position of the interface points in the G02 gallery and in the modulator
Water Cooling (WTCO):
1- Inlet/outlet manifold;
(All water hoses external to the modulator enclosure are within WP16 scope)
Water manifold
Water manifold

## Slide 19
Position of the interface points in the G02 gallery and in the modulator
RF cell Local Protection System (RF – LPS):
1- Remote hard control cable;
(this cable is under WP8 scope)
Controller crate
Controller crate

## Slide 20
Position of the interface points in the G02 gallery and in the modulator
Personal Safety System (PSS):
1- PSS control cable;
(this cable is under ICS/PSS scope)
PSS contactorbox
PSS contactor box

## Slide 21
Position of the interface points in the G02 gallery and in the modulator
ICS:
1- Ethernet remote fieldbus cable;
2- External pulse trigger cable;
(both cables are within ICS scope)
Controller crate
Controller crate